## Sheet1
| eq_id | circle | gmd | zone | substation | equipment | outage_time | restoration_time | duration | is_trip | event_info | mw_interruption | is_bus | is_transformer | is_line | is_scheduled | is_forced | is_project_work | outage_status_sum | is_restored
0 | 3739 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-04-01 09:28 | 2023-04-01 11:27 | 1:59 | 0 | Red hot | 20 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
1 | 3740 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-04-01 09:27 | 2023-04-01 11:29 | 2:02 | 0 | Red hot | 20 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
2 | 3759 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-04-01 09:30 | 2023-04-01 11:28 | 1:58 | 0 | Red hot | 20 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
3 | 3760 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-04-01 09:26 | 2023-04-01 11:30 | 2:04 | 0 | Red hot | 20 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
4 | 3819 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-04-20 23:05 | 2023-04-21 04:58 | 5:53 | 0 | According to NLDC's instruction. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
5 | 1940 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-04-17 08:45 | 2023-04-17 11:58 | 3:13 | 0 | T-2 blast wall work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
6 | 1941 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-04-17 08:45 | 2023-04-17 11:58 | 3:13 | 0 | T-2 blast wall work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
7 | 6676 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-04-12 15:27 | 2023-04-12 15:35 | 0:08 | 0 | For parallel operation T1 & T2 Xformar | 16 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
8 | 6676 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-04-17 14:09 | 2023-04-17 16:03 | 1:54 | 0 | 132kv CB r phase strand cutting | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
9 | 6687 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-04-20 09:41 | 2023-04-20 10:51 | 1:10 | 0 | High temperature @ T-3 132 KV CT Side (B-Phase) | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
10 | 6688 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-04-20 09:41 | 2023-04-20 10:51 | 1:10 | 0 | High temperature @ T-3 132 KV CT Side (B-Phase) | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
11 | 6699 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-04-20 09:29 | 2023-04-20 09:40 | 0:11 | 0 | T-3/T-4 Bus coupler because of T-3 Transformer S/D. | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
12 | 6700 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-4 LT | 2023-04-20 09:29 | 2023-04-20 09:40 | 0:11 | 0 | T-3/T-4 Bus coupler close because of T-3 Transformer S/D. | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
13 | 7840 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-1 | 2023-04-02 06:51 | 2023-04-02 17:23 | 10:32 | 0 | project work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
14 | 7842 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-2 | 2023-04-01 06:46 | 2023-04-01 18:23 | 11:37 | 0 | Tower Height Extension. | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
15 | 1944 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-04-07 11:03 | 2023-04-07 12:05 | 1:02 | 0 | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-01 Transformer. The involved distribution entity(PBS 1&2) has been informed about this matter over the phone & they have no objection to power interruption. | 30 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
16 | 1944 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-04-24 17:27 | 2023-04-24 17:43 | 0:16 | 1 | T1,132KV VCB trip due to PBS-1,33KV Raygonj feeder fault. | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
17 | 1945 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-04-07 11:02 | 2023-04-07 12:04 | 1:02 | 0 | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-01 Transformer. | 30 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
18 | 1945 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-04-24 17:27 | 2023-04-24 17:44 | 0:17 | 1 | T1,33KV VCB trip due to PBS-1,33KV Raygonj feeder fault. | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
19 | 2095 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T2-(425) HT | 2023-04-07 07:22 | 2023-04-07 08:56 | 1:34 | 0 | Red Hot has become visible/measured at different points of T-02 33kV BUS, CT, and DS at T-02 Transformer. | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
20 | 2096 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-04-07 07:21 | 2023-04-07 09:57 | 2:36 | 0 | Red Hot has become visible/measured at different points of T-02 33kV BUS, CT, and DS at T-02 Transformer. | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
21 | 2096 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-04-19 07:05 | 2023-04-19 07:30 | 0:25 | 0 | Red Hot has become visible/measured at 33kV T2+T3 connecting bus isolator. all operation has been conducted by the instruction of ALDC, Bogura with the permission of NLDC Dhaka. | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
22 | 2096 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-04-24 17:27 | 2023-04-24 17:42 | 0:15 | 1 | T2,33KV VCB trip due to PBS-1,33KV Raygonj feeder fault. | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
23 | 2296 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-01 14:26 | 2023-04-01 15:16 | 0:50 | 0 | Emergency Red Hot maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
24 | 2296 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-01 15:45 | 2023-04-01 17:30 | 1:45 | 0 | Red Hot Bolt replace at CT P2 end. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
25 | 2296 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-13 06:39 | 2023-04-13 08:28 | 1:49 | 0 | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-04 Transformer. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
26 | 2296 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-15 06:28 | 2023-04-15 11:00 | 4:32 | 0 | CB & CT connector change & replacing copper flexible conductor. | 12 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
27 | 2297 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-04-13 06:38 | 2023-04-13 08:29 | 1:51 | 0 | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-04 Transformer. | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
28 | 2297 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-04-15 06:27 | 2023-04-15 11:01 | 4:34 | 0 | CB & CT connector change & replacing copper flexible conductor. | 12 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
29 | 2320 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-04-04 11:35 | 2023-04-04 12:23 | 0:48 | 0 | a kite has been stuck to Sirajgonj- Sherpur ckt-02. For removing this kite Sirajgonj- Sherpur ckt-02 has been taken emergency shut down by the instruction of ALDC, Bogura. the shutdown request by Station in charge over the phone. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
30 | 2329 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-04-04 12:29 | 2023-04-04 12:41 | 0:12 | 0 | a kite has been stuck to Sirajgonj- Sherpur ckt-01. For removing this kite Sirajgonj- Sherpur ckt-01 has been taken emergency shut down by the instruction of ALDC, Bogura. the shutdown request by Station in charge over the phone.. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
31 | 2329 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-04-18 21:05 | 2023-04-19 07:38 | 10:33 | 0 | ALDC Bogura instruction Sirajgonj-Sherpur line (Ckt-1) CB off due to Pabna-Shahjadpur 132KV TL overload. | 14 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
32 | 7217 | Bogura | Bogura | Rajshahi | Sirajgonj 230 kV Switching Station | Baghabari -02 | 2023-04-15 10:54 | 2023-04-15 16:48 | 5:54 | 1 | Trip | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
33 | 1891 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus A | 2023-04-13 09:37 | 2023-04-13 11:03 | 1:26 | 0 | Red hat maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
34 | 7712 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T HT | 2023-04-13 09:42 | 2023-04-13 11:37 | 1:55 | 0 | Red hat maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
35 | 7713 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2023-04-13 09:42 | 2023-04-13 11:38 | 1:56 | 0 | Red hat maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
36 | 7721 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T HT | 2023-04-13 12:08 | 2023-04-16 14:48 | 74:40 | 0 | oil sentrifuse | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
37 | 7722 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2023-04-13 12:07 | 2023-04-16 14:53 | 74:46 | 0 | oil centrifuge | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
38 | 7844 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | PS 230 KV Ckt1 | 2023-04-11 21:25 | 2023-04-12 16:34 | 19:09 | 0 | Sky wire red hot | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
39 | 1916 | Bogura | Dinajpur | Rangpur | Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-04-07 07:40 | 2023-04-07 09:35 | 1:55 | 0 | 33KV BUS Corrective maintenance | 35 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
40 | 1917 | Bogura | Dinajpur | Rangpur | Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-04-07 07:40 | 2023-04-07 09:35 | 1:55 | 0 | 33KV BUS Corrective maintenance | 35 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
41 | 7799 | Bogura | Rajshahi | Rajshahi | Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-04-18 09:17 | 2023-04-18 10:48 | 1:31 | 0 | 33kV CT High Junction Temperature | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
42 | 7800 | Bogura | Rajshahi | Rajshahi | Chapai 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-04-18 09:17 | 2023-04-18 10:49 | 1:32 | 0 | Same | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
43 | 1522 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 HT | 2023-04-09 11:51 | 2023-04-10 00:38 | 12:47 | 0 | Emergency redhot maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
44 | 1523 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-04-09 11:49 | 2023-04-10 00:41 | 12:52 | 0 | Emergency redhot maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
45 | 1523 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-04-17 20:44 | 2023-04-17 20:56 | 0:12 | 1 | trip | 67 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
46 | 6356 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-04-02 06:50 | 2023-04-02 17:24 | 10:34 | 0 | project work of Bogura s/s. | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
47 | 6356 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-04-03 06:39 | 2023-04-03 14:27 | 7:48 | 0 | S/D for Bogura side | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
48 | 6356 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-04-04 07:25 | 2023-04-04 15:15 | 7:50 | 0 | bogura s/s reconducting work. | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
49 | 6362 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2023-04-01 06:46 | 2023-04-01 18:22 | 11:36 | 0 | Shutdown for Bogura side | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
50 | 1975 | Bogura | Rajshahi | Rajshahi | Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-04-13 17:49 | 2023-04-14 04:40 | 10:51 | 1 | Ishurdi end fault | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
51 | 2214 | Bogura | Rajshahi | Rajshahi | Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-04-13 17:49 | 2023-04-14 04:40 | 10:51 | 1 | Ishurdi end trip. | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
52 | 2214 | Bogura | Rajshahi | Rajshahi | Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-04-24 19:12 | 2023-04-24 19:19 | 0:07 | 1 | Wather cluudy,thandaring. | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
53 | 10531 | Bogura | Rajshahi | Rajshahi | Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-04-05 01:50 | 2023-04-05 17:04 | 15:14 | 0 | Red hot and Flashing at 33kv BUS side of Tr-02. | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
54 | 10531 | Bogura | Rajshahi | Rajshahi | Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-04-17 07:14 | 2023-04-17 16:28 | 9:14 | 0 | Transformer T-2 erection. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
55 | 10532 | Bogura | Rajshahi | Rajshahi | Niamatpur 132/33kV Grid Sub-Station | 417T LT | 2023-04-05 13:49 | 2023-04-05 17:04 | 3:15 | 0 | Red hot and Flashing at 33kv BUS side of Tr-02. | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
56 | 10532 | Bogura | Rajshahi | Rajshahi | Niamatpur 132/33kV Grid Sub-Station | 417T LT | 2023-04-17 07:14 | 2023-04-17 16:52 | 9:38 | 0 | Transformer T-2 erection. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
57 | 2868 | Bogura | Rajshahi | Rajshahi | Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-04-24 23:44 | 2023-04-25 01:25 | 1:41 | 0 | T-3 33KV B phase TDS red hot maintenance . | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
58 | 2869 | Bogura | Rajshahi | Rajshahi | Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-04-24 22:55 | 2023-04-25 01:33 | 2:38 | 0 | T-3 33KV B phase TDS red hot maintenance . | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
59 | 3747 | Bogura | Rajshahi | Rajshahi | Rajshahi 230/132/33kV Grid Sub-Station | T-01 (406T) HT | 2023-04-13 15:33 | 2023-04-13 17:33 | 2:00 | 0 | AUX-1Busing Y Phase Blast | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
60 | 3748 | Bogura | Rajshahi | Rajshahi | Rajshahi 230/132/33kV Grid Sub-Station | T-01 (406T) LT | 2023-04-13 15:33 | 2023-04-13 17:50 | 2:17 | 0 | AUX-1Busing Y Phase Blast | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
61 | 1954 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-04-12 09:44 | 2023-04-12 13:50 | 4:06 | 0 | Under Frequency Relay setting and testing of TR-1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
62 | 1955 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-01 04:42 | 2023-04-01 05:55 | 1:13 | 1 | Dabigonj-3, 33 KV feeder Fault for Bad Weather with Running and Tendering. | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
63 | 1955 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-12 09:43 | 2023-04-12 14:06 | 4:23 | 0 | Under Frequency Relay setting and testing of TR-1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
64 | 1955 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-13 13:37 | 2023-04-13 13:50 | 0:13 | 1 | under frequency | 26.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
65 | 1955 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-13 16:53 | 2023-04-13 16:58 | 0:05 | 1 | under frequency | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
66 | 5528 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 416T HT | 2023-04-12 14:15 | 2023-04-12 15:36 | 1:21 | 0 | Under frequency relay setting and testing of TR-2. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
67 | 5529 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-01 04:42 | 2023-04-01 05:57 | 1:15 | 1 | Dabigonj-3, 33 KV feeder Fault for Bad Weather with Running and Tendering. | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
68 | 5529 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-12 14:14 | 2023-04-12 15:37 | 1:23 | 0 | Under frequency relay setting and testing of TR-2. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
69 | 5529 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-13 13:37 | 2023-04-13 13:50 | 0:13 | 1 | under frequency | 26.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
70 | 5529 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-13 16:53 | 2023-04-13 16:58 | 0:05 | 1 | under frequency | 26.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
71 | 3613 | Bogura | Rangpur | Rangpur | Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) HT | 2023-04-07 08:14 | 2023-04-07 09:36 | 1:22 | 0 | For 33 kv feeder red hot maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
72 | 3614 | Bogura | Rangpur | Rangpur | Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-04-07 08:14 | 2023-04-07 09:36 | 1:22 | 0 | For 33 kv feeder red hot maintenance work. | 26 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
73 | 3615 | Bogura | Rangpur | Rangpur | Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) HT | 2023-04-07 08:15 | 2023-04-07 09:34 | 1:19 | 0 | For 33 kv feeder red hot maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
74 | 3616 | Bogura | Rangpur | Rangpur | Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-04-07 08:15 | 2023-04-07 09:34 | 1:19 | 0 | For 33 kv feeder red hot maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
75 | 6658 | Bogura | Rangpur | Rangpur | Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) HT | 2023-04-12 15:02 | 2023-04-12 16:38 | 1:36 | 0 | Due to clear of red hot at 33Kv busbar of NESCO, Saidpur | 28 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
76 | 6659 | Bogura | Rangpur | Rangpur | Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-04-12 15:01 | 2023-04-12 16:39 | 1:38 | 0 | NoneDue to clear of red hot at 33Kv busbar of NESCO, Saidpur | 28 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
77 | 2638 | Chattogram | Chattogram (Central) | Chattogram | Bakulia 132/33kV Grid Sub-Station | T-1 (402T) HT | 2023-04-06 19:10 | 2023-04-06 19:23 | 0:13 | 0 | Transformer tripped by O/C & E/F. | 10 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
78 | 2712 | Chattogram | Chattogram (Central) | Chattogram | Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2023-04-06 20:18 | 2023-04-07 00:43 | 4:25 | 0 | Red hot maintenance at Modern end. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
79 | 2716 | Chattogram | Chattogram (Central) | Chattogram | Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2023-04-07 07:04 | 2023-04-07 09:47 | 2:43 | 0 | Red hot maintenance at Khulshi end. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
80 | 4950 | Chattogram | Chattogram (Central) | Chattogram | Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2023-04-07 07:20 | 2023-04-07 09:41 | 2:21 | 0 | Khulshi 132/33 kV grid s/s end red hot | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
81 | 5016 | Chattogram | Chattogram (Central) | Chattogram | Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2023-04-09 17:54 | 2023-04-09 18:10 | 0:16 | 1 | Transient fault | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
82 | 5016 | Chattogram | Chattogram (Central) | Chattogram | Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2023-04-15 02:31 | 2023-04-15 03:34 | 1:03 | 1 | O/C Fault at B phase | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
83 | 1950 | Chattogram | Chattogram (Central) | Chattogram | Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2023-04-01 10:45 | 2023-04-01 11:43 | 0:58 | 0 | Red Hot Mantanance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
84 | 6821 | Chattogram | Chattogram (Central) | Chattogram | Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2023-04-15 03:13 | 2023-04-15 08:19 | 5:06 | 0 | Shahmirpur End Red Hot | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
85 | 1879 | Chattogram | Chattogram (Central) | Chattogram | Khulshi 132/33kV Grid Sub-Station | Main Bus | 2023-04-07 07:17 | 2023-04-07 09:34 | 2:17 | 0 | Red hot at khul-hal ckt-3 | 30 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
86 | 10470 | Chattogram | Chattogram (Central) | Chattogram | Modern Steel 132/11kV Grid Sub-Station | Modern Bakalia Ckt 2 | 2023-04-06 20:17 | 2023-04-07 00:45 | 4:28 | 0 | Red Hot is seen at the Cable clamp joint in the B phase of the 132kV Mod- Bak line at Modern Grid 132/11 kV Substation. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
87 | 4411 | Chattogram | Chattogram (Central) | Chattogram | Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2023-04-07 07:15 | 2023-04-07 09:50 | 2:35 | 0 | development work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
88 | 4412 | Chattogram | Chattogram (Central) | Chattogram | Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2023-04-07 07:19 | 2023-04-07 09:15 | 1:56 | 0 | development work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
89 | 11603 | Chattogram | Chattogram (North) | Chattogram | AKS 132/33kV Grid Sub-Station | Khulshi | 2023-04-07 07:20 | 2023-04-07 09:54 | 2:34 | 0 | Shutdown for Khulshi Demand. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
90 | 1544 | Chattogram | Chattogram (North) | Chattogram | Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2023-04-19 07:10 | 2023-04-19 09:38 | 2:28 | 0 | Red Hot in Line Isolator | 40 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
91 | 1817 | Chattogram | Chattogram (North) | Chattogram | Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2023-04-07 07:19 | 2023-04-07 09:25 | 2:06 | 0 | Working have to be done in Khulsi end | 40 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
92 | 1818 | Chattogram | Chattogram (North) | Chattogram | Baroaulia 132/33kV Grid Sub-Station | AKSPL | 2023-04-07 07:20 | 2023-04-07 09:58 | 2:38 | 0 | Working have to be done in Khulsi end | 20 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
93 | 4705 | Chattogram | Chattogram (North) | Chattogram | Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2023-04-15 16:42 | 2023-04-15 17:20 | 0:38 | 1 | DISTANCE Trip phase R&Y at Zone-2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
94 | 4706 | Chattogram | Chattogram (North) | Chattogram | Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-04-08 10:35 | 2023-04-08 12:47 | 2:12 | 0 | Emergency work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
95 | 4706 | Chattogram | Chattogram (North) | Chattogram | Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-04-15 16:42 | 2023-04-15 17:20 | 0:38 | 1 | DISTANCE Trip phase R&Y at Zone-2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
96 | 5758 | Chattogram | Chattogram (North) | Chattogram | BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-1 | 2023-04-12 11:10 | 2023-04-12 14:54 | 3:44 | 0 | Project work | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
97 | 5758 | Chattogram | Chattogram (North) | Chattogram | BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-1 | 2023-04-13 11:14 | 2023-04-13 14:54 | 3:40 | 0 | Work Done | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
98 | 5763 | Chattogram | Chattogram (North) | Chattogram | BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-2 | 2023-04-13 14:56 | 2023-04-13 16:17 | 1:21 | 0 | Work Done | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
99 | 8454 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2023-04-08 10:36 | 2023-04-08 12:47 | 2:11 | 0 | Bamboo trimming and removal from near to the line. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
100 | 8459 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Madunaghat GIS-01 | 2023-04-17 08:00 | 2023-04-17 17:05 | 9:05 | 0 | CT Change | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
101 | 11106 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | MT-04 HT | 2023-04-01 11:40 | 2023-04-01 14:09 | 2:29 | 0 | Red hot maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
102 | 11107 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | MT-04 LT | 2023-04-01 11:40 | 2023-04-01 14:10 | 2:30 | 0 | Red hot maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
103 | 9612 | Chattogram | Chattogram (North) | Chattogram | KSRM 132/33kV Grid Sub-Station | Baraulia Feeder | 2023-04-15 16:42 | 2023-04-15 17:58 | 1:16 | 1 | under frequency, grid failure ! | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
104 | 3842 | Chattogram | Chattogram (North) | Chattogram | Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-02 | 2023-04-10 10:42 | 2023-04-10 12:26 | 1:44 | 0 | Rangamati - Chandraghona Ckt-02 ,C.T-B-Phase red hot. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
105 | 7813 | Chattogram | Chattogram (North) | Chattogram | Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 2023-04-01 14:17 | 2023-04-01 16:03 | 1:46 | 0 | Tr-02(416T) 33kv "R" phase bushing oil leakage | 15 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
106 | 7814 | Chattogram | Chattogram (North) | Chattogram | Shahmirpur 132/33kV Grid Sub-Station | 416T LT | 2023-04-01 14:16 | 2023-04-01 16:06 | 1:50 | 0 | 33kv "R"phase bushing oil leakage | 15 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
107 | 10430 | Chattogram | Chattogram (North) | Chattogram | Shahmirpur 132/33kV Grid Sub-Station | Julda-2 | 2023-04-15 02:36 | 2023-04-15 08:17 | 5:41 | 0 | 213M/215G Line DS flashing at I clamp | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
108 | 5292 | Chattogram | Chattogram (South) | Chattogram | Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2023-04-04 13:05 | 2023-04-04 14:11 | 1:06 | 0 | Spare transformer T1 25/41 MVA Transfer. | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
109 | 5292 | Chattogram | Chattogram (South) | Chattogram | Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2023-04-13 22:03 | 2023-04-13 22:16 | 0:13 | 1 | Fault occured by 33 kv Rajastali feeder. Ins E/F. | 28 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
110 | 7807 | Chattogram | Chattogram (South) | Chattogram | Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2023-04-13 22:22 | 2023-04-13 22:31 | 0:09 | 1 | Over Current | 89 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
111 | 7807 | Chattogram | Chattogram (South) | Chattogram | Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2023-04-20 21:25 | 2023-04-20 21:30 | 0:05 | 1 | Overcurrent | 90 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
112 | 1648 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2023-04-05 08:38 | 2023-04-05 10:15 | 1:37 | 0 | SD Taken by Matarbari SS | 28 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
113 | 8392 | Chattogram | Chattogram (South) | Chattogram | Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2023-04-13 16:04 | 2023-04-13 17:01 | 0:57 | 0 | Maintainance | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
114 | 11917 | Chattogram | Chattogram (South) | Chattogram | Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2023-04-13 11:26 | 2023-04-13 16:04 | 4:38 | 0 | Maintainance | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
115 | 5174 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2023-04-15 16:42 | 2023-04-15 22:08 | 5:26 | 1 | General trip[zone-02(9km),R,Y,B phase Fault] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
116 | 5219 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-1 | 2023-04-15 16:42 | 2023-04-17 17:05 | 48:23 | 1 | General trip[R,Y,B phase fault,zcom/WET Trip] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
117 | 12073 | Chattogram | Chattogram (South) | Chattogram | Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 HT | 2023-04-01 07:20 | 2023-04-01 09:12 | 1:52 | 1 | Hathazari-shikolbaha ckt-2 trip. | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
118 | 12073 | Chattogram | Chattogram (South) | Chattogram | Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 HT | 2023-04-15 16:42 | 2023-04-15 18:58 | 2:16 | 1 | Hathazari - Shikalbaha Ckt-2 Trip | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
119 | 12074 | Chattogram | Chattogram (South) | Chattogram | Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 LT | 2023-04-01 07:20 | 2023-04-01 09:12 | 1:52 | 1 | Hathazari-shikolbaha ckt-2 trip. | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
120 | 12074 | Chattogram | Chattogram (South) | Chattogram | Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 LT | 2023-04-15 16:42 | 2023-04-15 17:50 | 1:08 | 1 | Hathazari - Shikalbaha Ckt -2 trip | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
121 | 4617 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Interconnection-1 | 2023-04-17 16:01 | 2023-04-18 10:42 | 18:41 | 0 | Emergency maintenance at Shikalbaha 132 KV end. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
122 | 10636 | Cumilla | Cumilla | Cumilla | Chandpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2023-04-11 15:39 | 2023-04-11 16:44 | 1:05 | 0 | SF6 gas filling | 71 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
123 | 1627 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 HT | 2023-04-18 12:00 | 2023-04-18 13:03 | 1:03 | 0 | 33 kv Bus-01 red hot | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
124 | 1628 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 LT | 2023-04-18 12:01 | 2023-04-18 13:03 | 1:02 | 0 | 33 kv Bus-01 Red Hot. | 20 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
125 | 3145 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | Feni-1 | 2023-04-23 05:03 | 2023-04-23 08:40 | 3:37 | 0 | to reduced over load cumilla north 230/132 kv transformer by the command of XEN,(NOD),NLDC. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
126 | 5032 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2023-04-02 10:24 | 2023-04-02 11:53 | 1:29 | 0 | 33KV Balutopa Feeder BUS Isulator Problem. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
127 | 5032 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2023-04-15 22:59 | 2023-04-15 23:45 | 0:46 | 0 | Red hot remove. | 40 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
128 | 5033 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-04-02 10:24 | 2023-04-02 11:53 | 1:29 | 0 | 33KV Balutopa Feeder BUS Isulator Problem. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
129 | 5033 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-04-15 22:59 | 2023-04-15 23:45 | 0:46 | 0 | Red hot remove. | 40 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
130 | 2580 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2023-04-20 05:58 | 2023-04-20 07:59 | 2:01 | 0 | Red hot Maintenance | 38 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
131 | 2581 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-04-20 05:57 | 2023-04-20 07:59 | 2:02 | 0 | 33Kv CT terminal R ph Red hot. | 38 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
132 | 2586 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-3 HT | 2023-04-06 19:12 | 2023-04-06 19:23 | 0:11 | 0 | load shift from India grid to BD grid | 24 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
133 | 2587 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-3 LT | 2023-04-06 14:12 | 2023-04-06 19:23 | 5:11 | 0 | load shift from India grid to BD grid | 24 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
134 | 8574 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-04-21 17:48 | 2023-04-21 19:07 | 1:19 | 1 | Heavy Storm | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
135 | 1740 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-04-15 05:48 | 2023-04-15 11:20 | 5:32 | 0 | 33 kv Bus loop & 33 kv bus DS Y Phase (Capacitor Bank) Replacement work | 25 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
136 | 1740 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-04-20 06:32 | 2023-04-20 08:42 | 2:10 | 0 | 33kv bus s/down (T-1) for chow ckt-1 bus DS maintenance work. S/D taken BPDB. | 32 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
137 | 9268 | Cumilla | Cumilla | Cumilla | Kachua 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-08 10:31 | 2023-04-08 17:49 | 7:18 | 0 | Rectification of auxiliary TR-1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
138 | 9269 | Cumilla | Cumilla | Cumilla | Kachua 132/33kV Grid Sub-Station | TR-1 LT | 2023-04-08 10:30 | 2023-04-08 17:50 | 7:20 | 0 | Rectification of auxiliary TR-1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
139 | 9270 | Cumilla | Cumilla | Cumilla | Kachua 132/33kV Grid Sub-Station | TR-2 HT | 2023-04-23 22:17 | 2023-04-24 10:49 | 12:32 | 1 | pt fault | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
140 | 9271 | Cumilla | Cumilla | Cumilla | Kachua 132/33kV Grid Sub-Station | TR-2 LT | 2023-04-23 22:17 | 2023-04-24 10:51 | 12:34 | 1 | pt fault | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
141 | 2677 | Cumilla | Cumilla | Cumilla | Ramganj 132/33kV Grid Sub-Station | Transformer-01 LT | 2023-04-10 07:37 | 2023-04-10 08:58 | 1:21 | 0 | Red hot maintenance work. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
142 | 4792 | Cumilla | Cumilla | Cumilla | Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2023-04-11 07:45 | 2023-04-11 09:08 | 1:23 | 0 | red hot & temperature raising point maintenance. | 20 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
143 | 4793 | Cumilla | Cumilla | Cumilla | Ramganj 132/33kV Grid Sub-Station | Transformer -02 LT | 2023-04-11 07:45 | 2023-04-11 09:08 | 1:23 | 0 | Temperature raising point & Red hot maintenance. | 20 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
144 | 11272 | Cumilla | Srimongol | Sylhet | Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-II | 2023-04-04 09:39 | 2023-04-04 12:43 | 3:04 | 0 | Maintenance work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
145 | 11282 | Cumilla | Srimongol | Sylhet | Bibiana 400/230kV Sub-Station | Bibiyana-III (Back feed) | 2023-04-02 14:25 | 2023-04-05 16:16 | 73:51 | 1 | Inter trip From power station | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
146 | 9278 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2023-04-15 11:21 | 2023-04-15 12:19 | 0:58 | 0 | Bus section -5 maintenance work by PDB division -1. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
147 | 9279 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-04-15 11:20 | 2023-04-15 12:19 | 0:59 | 0 | Bus section -5 maintenance work by PDB division -1. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
148 | 9291 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-04-06 14:14 | 2023-04-06 14:29 | 0:15 | 1 | Earth Fault & overcurrent | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
149 | 9291 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-04-16 08:16 | 2023-04-16 14:47 | 6:31 | 0 | instruction by NLDC. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
150 | 9815 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Aux. Tr-2 (PGCB) LT | 2023-04-15 11:20 | 2023-04-15 12:30 | 1:10 | 0 | Bus section -5 maintenance work by PDB division -1. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
151 | 5608 | Cumilla | Srimongol | Sylhet | Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-04 11:44 | 2023-04-04 12:32 | 0:48 | 0 | Red hot maintenance of REB Feeder-2. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
152 | 5608 | Cumilla | Srimongol | Sylhet | Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-05 23:17 | 2023-04-06 00:34 | 1:17 | 0 | For red hot maintenance by REB. | 14 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
153 | 5608 | Cumilla | Srimongol | Sylhet | Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-08 10:48 | 2023-04-08 13:00 | 2:12 | 0 | Red hot maintenance by REB 1& REB 2. | 12 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
154 | 5609 | Cumilla | Srimongol | Sylhet | Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-04-05 23:17 | 2023-04-06 00:34 | 1:17 | 0 | For red hot maintenance by REB. | 14 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
155 | 5609 | Cumilla | Srimongol | Sylhet | Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-04-08 10:48 | 2023-04-08 13:00 | 2:12 | 0 | Red hot maintenance by REB 1& REB 2. | 12 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
156 | 1953 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-04-02 20:22 | 2023-04-02 20:29 | 0:07 | 1 | Due to shaistaganj feeder fault. | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
157 | 2369 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-04-15 06:28 | 2023-04-15 08:05 | 1:37 | 0 | 132 KV side ring bus R phase red hot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
158 | 2369 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-04-18 23:14 | 2023-04-18 23:56 | 0:42 | 0 | TR-04 33 kv side bus shutdown due to hobigonj old feeder redhot maintenance. | 45 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
159 | 2370 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-04-18 23:11 | 2023-04-18 23:59 | 0:48 | 0 | 33 kv Hobigonj old feeder redhot maintenance. | 45 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
160 | 2399 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-06 HT | 2023-04-01 09:15 | 2023-04-01 10:54 | 1:39 | 0 | Jamuna feeder red hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
161 | 2400 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2023-04-01 09:14 | 2023-04-01 10:55 | 1:41 | 0 | Jumuna feeder red hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
162 | 2523 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-04-03 04:46 | 2023-04-03 04:57 | 0:11 | 1 | Stormy Wether | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
163 | 3371 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2023-04-16 23:45 | 2023-04-18 14:30 | 38:45 | 0 | Tr-3 33kV CT Redhot. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
164 | 3372 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-04-16 23:42 | 2023-04-18 14:30 | 38:48 | 0 | Tr-3 33kV CT Redhot. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
165 | 3390 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | sreemangal-Shahjibazar circuit-2 | 2023-04-03 04:46 | 2023-04-03 04:57 | 0:11 | 1 | heavy raining and thunder. | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
166 | 3395 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-04-21 19:55 | 2023-04-21 19:59 | 0:04 | 1 | Thundering. | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
167 | 3395 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-04-22 02:28 | 2023-04-22 03:55 | 1:27 | 0 | For removing the torn OPGW cable from line. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
168 | 3395 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-04-23 07:42 | 2023-04-23 22:39 | 14:57 | 0 | OPGW cable connection Works . | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
169 | 3400 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-04-22 02:28 | 2023-04-22 03:55 | 1:27 | 0 | For removing the torn OPGW cable from line. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
170 | 3400 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-04-23 07:42 | 2023-04-23 22:39 | 14:57 | 0 | OPGW cable connection Works | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
171 | 7803 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2023-04-06 10:59 | 2023-04-06 12:33 | 1:34 | 0 | None | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
172 | 7804 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2023-04-06 10:58 | 2023-04-06 12:34 | 1:36 | 0 | None | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
173 | 11958 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-04-17 09:15 | 2023-04-17 16:51 | 7:36 | 0 | Sylhet ckt-1 CB replace work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
174 | 11958 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-04-18 08:23 | 2023-04-18 22:12 | 13:49 | 0 | Sylhet-chhatak Ckt-1 CB replace work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
175 | 11958 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-04-19 07:14 | 2023-04-19 11:05 | 3:51 | 0 | New Breaker Replacement | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
176 | 11995 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | Sunamganj 1 | 2023-04-03 10:05 | 2023-04-03 10:13 | 0:08 | 1 | None | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
177 | 1639 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-04-22 02:29 | 2023-04-22 03:48 | 1:19 | 0 | OPGW Fault restoration work | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
178 | 1639 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-04-23 07:46 | 2023-04-23 22:40 | 14:54 | 0 | OPGW restoration | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
179 | 1641 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-04-22 02:29 | 2023-04-22 03:48 | 1:19 | 0 | OPGW Fault Restoration work | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
180 | 1641 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-04-23 07:47 | 2023-04-23 22:40 | 14:53 | 0 | OPGW Restoration | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
181 | 1644 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-04-05 11:25 | 2023-04-05 11:30 | 0:05 | 1 | Due to bad weather | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
182 | 1644 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-04-05 11:31 | 2023-04-05 11:40 | 0:09 | 0 | Maintenance | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
183 | 4294 | Cumilla | Sylhet | Sylhet | Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-04-03 10:07 | 2023-04-03 10:16 | 0:09 | 1 | Unknown | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
184 | 6758 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-04-17 09:24 | 2023-04-17 16:51 | 7:27 | 0 | Due to CB Replace | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
185 | 6758 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-04-18 08:28 | 2023-04-18 22:12 | 13:44 | 0 | work of chhatak end | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
186 | 6758 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-04-19 07:17 | 2023-04-19 11:03 | 3:46 | 0 | Maintenance for Chhatak SS end. | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
187 | 6782 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T2 HT | 2023-04-21 07:14 | 2023-04-21 07:58 | 0:44 | 1 | o/c, E/F,87 signal , 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 65 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
188 | 6783 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T2 LT | 2023-04-21 07:14 | 2023-04-21 08:37 | 1:23 | 1 | 51n.50,87 signal. 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
189 | 6785 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T4 HT | 2023-04-21 07:14 | 2023-04-21 08:02 | 0:48 | 1 | genaral prip signa. 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
190 | 6786 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-04-21 07:14 | 2023-04-21 08:02 | 0:48 | 1 | genaral trip. 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
191 | 22 | Dhaka (N) | Aricha | Dhaka | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-04-16 08:38 | 2023-04-16 11:11 | 2:33 | 0 | Pbs works | 10 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
192 | 23 | Dhaka (N) | Aricha | Dhaka | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-04-16 08:38 | 2023-04-16 11:11 | 2:33 | 0 | Pbs works | 10 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
193 | 10011 | Dhaka (N) | Aricha | Dhaka | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-04-08 08:30 | 2023-04-08 11:32 | 3:02 | 0 | PBS Bus Maintenance work. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
194 | 37 | Dhaka (N) | Dhaka (North) | Mymensingh | Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2023-04-11 10:15 | 2023-04-11 11:44 | 1:29 | 0 | Relay Testing and df/dt setting implementation | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
195 | 63 | Dhaka (N) | Dhaka (North) | Mymensingh | Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-04-11 11:47 | 2023-04-11 11:56 | 0:09 | 0 | Relay testing and df/dt setting implementation | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
196 | 870 | Dhaka (N) | Dhaka (North) | Dhaka | Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-04-15 10:39 | 2023-04-15 11:16 | 0:37 | 0 | High temperature maintenance. | 40 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
197 | 872 | Dhaka (N) | Dhaka (North) | Dhaka | Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2023-04-25 09:35 | 2023-04-25 13:58 | 4:23 | 0 | Due to Test (Maintenance) Temperature Sensor. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
198 | 317 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Bus-1 | 2023-04-09 06:36 | 2023-04-09 08:41 | 2:05 | 1 | Try to open live DS by PBS | 33 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
199 | 318 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Bus-2 | 2023-04-09 06:36 | 2023-04-09 08:45 | 2:09 | 1 | Try open live DS by PBS | 114 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
200 | 348 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-04-03 12:15 | 2023-04-03 16:26 | 4:11 | 0 | DS work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
201 | 348 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-04-04 06:00 | 2023-04-04 06:14 | 0:14 | 0 | DS work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
202 | 348 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-04-09 06:17 | 2023-04-09 06:28 | 0:11 | 0 | Ds work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
203 | 349 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-04-03 12:15 | 2023-04-03 16:29 | 4:14 | 0 | DS work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
204 | 349 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-04-04 05:59 | 2023-04-04 06:15 | 0:16 | 0 | DS work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
205 | 349 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-04-09 06:17 | 2023-04-09 06:29 | 0:12 | 0 | Ds work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
206 | 352 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-04-03 05:35 | 2023-04-03 07:49 | 2:14 | 0 | 33Kv Bus DS maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
207 | 352 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-04-09 06:19 | 2023-04-09 14:38 | 8:19 | 0 | Ds work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
208 | 352 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-04-13 06:22 | 2023-04-13 09:06 | 2:44 | 0 | None | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
209 | 353 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-04-03 05:35 | 2023-04-03 07:54 | 2:19 | 0 | Bus DS Maintenance | 15 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
210 | 353 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-04-09 06:18 | 2023-04-09 14:39 | 8:21 | 0 | Ds work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
211 | 353 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-04-13 06:21 | 2023-04-13 09:07 | 2:46 | 0 | 33 kv T-02 BDS-1 Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
212 | 354 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2023-04-04 06:00 | 2023-04-04 08:18 | 2:18 | 0 | DS work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
213 | 355 | Dhaka (N) | Dhaka (North) | Dhaka | Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2023-04-04 05:59 | 2023-04-04 08:18 | 2:19 | 0 | DS work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
214 | 1450 | Dhaka (N) | Dhaka (North) | Dhaka | New Tongi 132/33kV Grid Sub-Station | Bus-1 | 2023-04-25 09:34 | 2023-04-25 13:18 | 3:44 | 0 | Reduce the excessive heat of L-2 (Line BUS DS-201M ). | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
215 | 1465 | Dhaka (N) | Dhaka (North) | Dhaka | New Tongi 132/33kV Grid Sub-Station | New Tongi L-2 | 2023-04-25 09:33 | 2023-04-25 13:15 | 3:42 | 0 | Reduce the excessive heat of L-2 (Line BUS DS-201M ). | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
216 | 1468 | Dhaka (N) | Dhaka (North) | Dhaka | New Tongi 132/33kV Grid Sub-Station | T2(413T) HT | 2023-04-25 09:32 | 2023-04-25 13:16 | 3:44 | 0 | Reduce the excessive heat of TR-2 transformer LT side (R-phase) | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
217 | 1469 | Dhaka (N) | Dhaka (North) | Dhaka | New Tongi 132/33kV Grid Sub-Station | T2(413T) LT | 2023-04-25 09:31 | 2023-04-25 13:17 | 3:46 | 0 | Reduce the excessive heat of TR-2 transformer LT side (R-phase) | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
218 | 12300 | Dhaka (N) | Dhaka (North) | Dhaka | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-04-04 09:43 | 2023-04-04 10:42 | 0:59 | 0 | Project work | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
219 | 12301 | Dhaka (N) | Dhaka (North) | Dhaka | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-04-04 09:43 | 2023-04-04 10:43 | 1:00 | 0 | Project work | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
220 | 12306 | Dhaka (N) | Dhaka (North) | Dhaka | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-04-04 10:45 | 2023-04-04 12:25 | 1:40 | 0 | Project work | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
221 | 12307 | Dhaka (N) | Dhaka (North) | Dhaka | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-04-04 10:45 | 2023-04-04 12:25 | 1:40 | 0 | Project Work | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
222 | 1170 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | 230 kV Bus-2 | 2023-04-04 08:12 | 2023-04-04 12:05 | 3:53 | 0 | None | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
223 | 1179 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2023-04-17 06:10 | 2023-04-17 07:45 | 1:35 | 0 | Maintenance work for rising temperature | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
224 | 1180 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2023-04-17 06:10 | 2023-04-17 07:45 | 1:35 | 0 | Maintenance work for rising temperature | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
225 | 1199 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2023-04-01 14:07 | 2023-04-01 14:45 | 0:38 | 1 | None | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
226 | 1200 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2023-04-01 14:07 | 2023-04-01 14:47 | 0:40 | 1 | None | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
227 | 1201 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2023-04-01 14:07 | 2023-04-01 14:41 | 0:34 | 1 | None | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
228 | 1202 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Kaliakoir Ckt | 2023-04-04 08:12 | 2023-04-04 08:32 | 0:20 | 1 | None | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
229 | 1203 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-04-01 12:01 | 2023-04-01 12:35 | 0:34 | 0 | Shutdown taken by Kabirpur | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
230 | 1207 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-04-17 19:10 | 2023-04-17 21:05 | 1:55 | 0 | Temperature rise Bashundhara end(Red hot). | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
231 | 1208 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-04-12 13:22 | 2023-04-12 15:33 | 2:11 | 0 | Remove of red hot work | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
232 | 576 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-04-16 12:23 | 2023-04-16 13:33 | 1:10 | 0 | 400/132 kV New ATR installation work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
233 | 576 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-04-18 09:18 | 2023-04-18 13:43 | 4:25 | 0 | Cable loop repairung of 132 kv side of 400/132 kv transforner | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
234 | 577 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-04-16 11:18 | 2023-04-16 12:01 | 0:43 | 0 | 400/132 kV New ATR installation work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
235 | 578 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-04-09 10:32 | 2023-04-09 16:32 | 6:00 | 0 | 230KVATR1 DS Modifying | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
236 | 11189 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-02 | 2023-04-01 10:20 | 2023-04-01 17:03 | 6:43 | 0 | Dead line cheking | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
237 | 11986 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-06 09:54 | 2023-04-07 12:20 | 26:26 | 0 | 400KV Jack Bus erection work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
238 | 11986 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-12 11:04 | 2023-04-12 19:36 | 8:32 | 0 | 400/132 kV New ATR installation work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
239 | 11986 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-15 14:04 | 2023-04-15 19:49 | 5:45 | 0 | 400/132 KV ATR loop connection | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0
240 | 11986 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-16 15:52 | 2023-04-16 17:47 | 1:55 | 0 | 400/132 kV New ATR installation | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
241 | 11986 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-17 14:52 | 2023-04-17 18:07 | 3:15 | 0 | Interim 400/132 kV ATR testing | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
242 | 11987 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2023-04-05 11:28 | 2023-04-05 13:08 | 1:40 | 0 | CSD Test | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
243 | 11988 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2023-04-05 11:25 | 2023-04-05 12:48 | 1:23 | 0 | CSD test | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
244 | 11989 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 HT | 2023-04-05 06:06 | 2023-04-05 11:09 | 5:03 | 0 | CSD Test | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
245 | 11990 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2023-04-05 06:03 | 2023-04-05 11:10 | 5:07 | 0 | CSD Test | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
246 | 11991 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-1 | 2023-04-06 07:09 | 2023-04-06 08:54 | 1:45 | 0 | CSD Test | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
247 | 11991 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-1 | 2023-04-16 09:56 | 2023-04-16 15:49 | 5:53 | 0 | 400/132 kV New ATR installation work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
248 | 11992 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-04-04 10:12 | 2023-04-04 13:29 | 3:17 | 0 | CSD Commissioning | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
249 | 11992 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-04-04 13:46 | 2023-04-04 17:19 | 3:33 | 0 | CSD Test | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
250 | 11992 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-04-09 07:29 | 2023-04-09 12:31 | 5:02 | 0 | commissioning (CSD test) | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
251 | 1106 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2023-04-10 07:01 | 2023-04-10 10:01 | 3:00 | 0 | Red Hot,Oile Level maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
252 | 1108 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-04-15 07:46 | 2023-04-15 09:03 | 1:17 | 0 | CT maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
253 | 1108 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-04-18 15:15 | 2023-04-18 15:25 | 0:10 | 0 | Sf6 gas pressure checking | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
254 | 1110 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2023-04-10 10:02 | 2023-04-10 11:14 | 1:12 | 0 | Filling oil in conservator tank | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
255 | 1124 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2023-04-11 07:53 | 2023-04-11 09:05 | 1:12 | 0 | Reduce high temperature at BkR down loop point. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
256 | 722 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-04-13 08:38 | 2023-04-13 12:55 | 4:17 | 0 | Hotspot maintenance on 33kV POTHEAD by Desco | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
257 | 723 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-04-13 08:35 | 2023-04-13 12:58 | 4:23 | 0 | Hotspot maintenance on 33kV POTHEAD by Desco | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
258 | 728 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2023-04-18 06:32 | 2023-04-18 06:55 | 0:23 | 0 | Amin Bazer Ss 400/132 Kv X-former commissioning work. | 62 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
259 | 729 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-04-18 08:04 | 2023-04-18 08:22 | 0:18 | 1 | Amin Bazer 400KV X-former Comissioning Effect. | 67 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
260 | 736 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2023-04-07 09:11 | 2023-04-07 16:05 | 6:54 | 0 | Dead line checking | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
261 | 125 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | Bus-A | 2023-04-10 09:50 | 2023-04-10 11:24 | 1:34 | 0 | red hot maintenance of 33kV Bus Isolator of 33kV L-32, L-36 & L-42 Feeder by PBS. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
262 | 758 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-04-11 09:06 | 2023-04-11 12:15 | 3:09 | 0 | TR-3 33 KV EPZ and Nayerhat feeder maintenance. | 80 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
263 | 759 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2023-04-11 09:05 | 2023-04-11 12:16 | 3:11 | 0 | TR-3 33 KV EPZ and Nayerhat feeder maintenance. | 80 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
264 | 11870 | Dhaka (N) | Kaliakoir | Dhaka | Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2023-04-04 09:35 | 2023-04-04 12:44 | 3:09 | 0 | By NLDC | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
265 | 493 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-04-05 09:27 | 2023-04-05 11:20 | 1:53 | 0 | 33 KV Bus coupler Maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
266 | 494 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-04-05 09:27 | 2023-04-05 11:20 | 1:53 | 0 | 33 KV Bus coupler Maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
267 | 494 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-04-07 05:17 | 2023-04-07 06:27 | 1:10 | 1 | Due to 33 kv Sk-vita-2 Feeder fault. | 35 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
268 | 494 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-04-16 03:07 | 2023-04-16 03:25 | 0:18 | 1 | 33Kv Nandina & Gopalpur feeder E/F ,O/C fault , then T-1 & T-2 LT side trip | 73 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
269 | 503 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-04-05 09:27 | 2023-04-05 11:20 | 1:53 | 0 | 33 KV Bus coupler Maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
270 | 503 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-04-18 07:32 | 2023-04-18 08:37 | 1:05 | 0 | Maintenance work due to temperature increase of 33kv CB connector. | 6 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
271 | 504 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-05 09:27 | 2023-04-05 11:20 | 1:53 | 0 | 33 KV Bus coupler Maintenance work | 13 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
272 | 504 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-07 05:17 | 2023-04-07 06:27 | 1:10 | 1 | Due to 33 kv Sk-vita-2 Feeder fault. | 35 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
273 | 504 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-16 03:07 | 2023-04-16 03:25 | 0:18 | 1 | 33Kv Nandina & Gopalpur feeder E/F ,O/C fault , then T-1 & T-2 LT side trip | 73 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
274 | 504 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-18 07:32 | 2023-04-18 08:37 | 1:05 | 0 | Maintenance work due to temperature increase of 33kv CB connector. | 6 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
275 | 513 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-04-16 09:49 | 2023-04-16 11:21 | 1:32 | 0 | High Temperature Work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
276 | 514 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | T-3 LT | 2023-04-16 09:49 | 2023-04-16 11:21 | 1:32 | 0 | High Temperature work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
277 | 248 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-04-01 19:29 | 2023-04-01 19:50 | 0:21 | 0 | Hotspot maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
278 | 248 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-04-08 08:22 | 2023-04-08 17:10 | 8:48 | 0 | T-3(B) Removal works from system | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
279 | 249 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2023-04-01 19:29 | 2023-04-01 19:50 | 0:21 | 0 | Hotspot maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
280 | 249 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2023-04-08 08:22 | 2023-04-08 17:20 | 8:58 | 0 | T-3(B) Removal works from system | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
281 | 10482 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | 33 kV T2 Bus | 2023-04-25 15:15 | 2023-04-25 15:37 | 0:22 | 0 | PDB will do Red-hot Maintenance | 50 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
282 | 78 | Dhaka (N) | Mymensingh | Mymensingh | Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2023-04-17 08:28 | 2023-04-17 09:47 | 1:19 | 0 | Maintanance Work. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
283 | 918 | Dhaka (N) | Mymensingh | Mymensingh | Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-01 | 2023-04-22 09:10 | 2023-04-22 10:00 | 0:50 | 1 | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
284 | 924 | Dhaka (N) | Mymensingh | Mymensingh | Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-04-08 23:43 | 2023-04-09 00:30 | 0:47 | 0 | Bay -03 bus to ds incoming red hot. | 46 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
285 | 185 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2023-04-16 22:38 | 2023-04-16 23:53 | 1:15 | 0 | Line CT of 33kV Shakhipur feeder is redhot | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
286 | 186 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2023-04-16 22:37 | 2023-04-16 23:55 | 1:18 | 0 | Line CT of 33kV Shakhipur feeder is redhot | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
287 | 188 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-04-08 12:11 | 2023-04-08 13:22 | 1:11 | 0 | Tree Trimining | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
288 | 188 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-04-08 13:59 | 2023-04-08 20:39 | 6:40 | 1 | fault at RPCL end | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
289 | 189 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-04-08 15:24 | 2023-04-08 16:09 | 0:45 | 1 | NLDC order | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
290 | 189 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-04-08 16:22 | 2023-04-08 16:39 | 0:17 | 1 | 132KV T4 R-phase LA Blast | 50 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
291 | 1822 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-04-01 15:27 | 2023-04-02 09:50 | 18:23 | 0 | OPG Cable joint and maintenance. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
292 | 1822 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-04-22 15:50 | 2023-04-22 18:48 | 2:58 | 0 | To remove long nylon net on top of tower no. 29 of Maniknagar Matuail Ckt. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
293 | 1824 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2023-04-01 15:42 | 2023-04-02 09:19 | 17:37 | 0 | OPG Cable joint and maintenance. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
294 | 7724 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2023-04-21 17:38 | 2023-04-21 23:38 | 6:00 | 1 | Stormy Rain | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
295 | 7725 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) LT | 2023-04-21 17:38 | 2023-04-21 23:43 | 6:05 | 1 | Stormy Rain | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
296 | 10258 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2023-04-09 06:15 | 2023-04-19 07:54 | 241:39 | 0 | Tower Erection | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
297 | 1437 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 2023-04-15 23:04 | 2023-04-16 23:11 | 24:07 | 0 | Gulshan CT & uper loop conducter Replace. | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
298 | 1437 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 2023-04-17 10:16 | 2023-04-17 12:47 | 2:31 | 0 | Protection team testing work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
299 | 3280 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2023-04-24 07:25 | 2023-04-24 20:03 | 12:38 | 0 | 230 kV Bhulta ckt.-02 Line CT-2338 ( Y -phase ) CT Replace . | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
300 | 3286 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-01 | 2023-04-15 23:01 | 2023-04-16 22:58 | 23:57 | 0 | GULshan -01 C T & uper conducter replace | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
301 | 6125 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-04-11 14:13 | 2023-04-11 14:27 | 0:14 | 1 | Unknown | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
302 | 6137 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Moghbazar-01 | 2023-04-05 05:34 | 2023-04-05 06:58 | 1:24 | 0 | Shutdown by NLDC | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
303 | 8710 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-04-15 06:09 | 2023-04-15 06:24 | 0:15 | 1 | None | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
304 | 8713 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-04-01 15:24 | 2023-04-02 09:22 | 17:58 | 0 | Work on other side by NLDC | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
305 | 8713 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-04-21 17:34 | 2023-04-21 17:55 | 0:21 | 1 | Thunderstorm. | 50 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
306 | 11946 | Dhaka (S) | Dhaka (East) | Dhaka | Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2023-04-21 17:53 | 2023-04-21 22:19 | 4:26 | 1 | Heavy rain,storm | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
307 | 11947 | Dhaka (S) | Dhaka (East) | Dhaka | Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-2 | 2023-04-21 17:53 | 2023-04-22 02:36 | 8:43 | 1 | Heavy rain,storm | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
308 | 12041 | Dhaka (S) | Dhaka (East) | Dhaka | Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-04-21 17:40 | 2023-04-22 19:14 | 25:34 | 1 | Heavy rain,storm | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
309 | 2359 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2023-04-21 17:33 | 2023-04-21 20:40 | 3:07 | 1 | Distance relay operated during heavy storm condition | 47 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
310 | 2362 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-04-21 17:45 | 2023-04-21 18:14 | 0:29 | 1 | Earth fault due to heavy storm | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
311 | 2364 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-04-21 17:45 | 2023-04-21 18:49 | 1:04 | 1 | storm wearher | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
312 | 2368 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 1 | 2023-04-06 09:27 | 2023-04-06 16:53 | 7:26 | 0 | Relay Change | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
313 | 2124 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 230/132kV Grid Sub-Station | MTR 1 HT | 2023-04-06 09:28 | 2023-04-06 16:53 | 7:25 | 0 | Relay changing work. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
314 | 5267 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Duadkandi 1 | 2023-04-03 08:35 | 2023-04-03 09:12 | 0:37 | 1 | Trip | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
315 | 5267 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Duadkandi 1 | 2023-04-05 10:58 | 2023-04-05 11:26 | 0:28 | 0 | Emergency maintenance work of Daudkanti-01. Y-ph lower plate CB insulator nut-bolt temperature high. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
316 | 3354 | Dhaka (S) | Dhaka (South) | Dhaka | Hasnabad 132/33kV Grid Substation | Shitallakhya | 2023-04-22 00:40 | 2023-04-22 01:30 | 0:50 | 0 | shytdown taken by shitallakhya for emergency maintenance work. | 25 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
317 | 10769 | Dhaka (S) | Dhaka (South) | Dhaka | Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2023-04-01 10:13 | 2023-04-01 17:05 | 6:52 | 0 | Dead line checking at Aminbazar end. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
318 | 3349 | Dhaka (S) | Dhaka (South) | Dhaka | Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj Ckt-1 | 2023-04-21 17:53 | 2023-04-21 22:20 | 4:27 | 1 | Rainstorm | 88 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
319 | 3350 | Dhaka (S) | Dhaka (South) | Dhaka | Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj- Ckt-2 | 2023-04-21 17:53 | 2023-04-22 02:34 | 8:41 | 1 | Heavy Rainstorm | 44 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
320 | 6571 | Dhaka (S) | Dhaka (South) | Dhaka | Shyampur 230/132kV Grid Sub-Station | 132 kV Fatullah-1(E06) | 2023-04-06 09:33 | 2023-04-06 12:05 | 2:32 | 0 | Due to Brid nesting | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
321 | 5916 | Dhaka (S) | Narsingdi | Dhaka | Bhulta 400/230kV Grid Sub-Station | Rampura-01 | 2023-04-02 18:26 | 2023-04-03 09:19 | 14:53 | 1 | Y-Phase trip, 67N trip, CR/DTT Received, General Trip | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
322 | 5917 | Dhaka (S) | Narsingdi | Dhaka | Bhulta 400/230kV Grid Sub-Station | Rampura-02 | 2023-04-23 20:41 | 2023-04-24 20:02 | 23:21 | 0 | CT fault at Rampura 230/132 kV Grid Sub-station. | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
323 | 1957 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | T-1 HT | 2023-04-16 19:40 | 2023-04-16 19:50 | 0:10 | 1 | time delay over current with earth fault relay | 63 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
324 | 1957 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | T-1 HT | 2023-04-19 13:33 | 2023-04-19 13:56 | 0:23 | 1 | 51HV Tripp. | 58 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
325 | 5270 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2023-04-22 15:02 | 2023-04-22 15:37 | 0:35 | 0 | Tr-02 (33kV) Incomer CT B-phase loop connection point oil leakage. | 30 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
326 | 5279 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | Haripur | 2023-04-10 13:13 | 2023-04-10 13:35 | 0:22 | 1 | Unknown | 94 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
327 | 5279 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | Haripur | 2023-04-15 06:09 | 2023-04-15 06:25 | 0:16 | 1 | CB Not Trip but Voltage Zero. | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
328 | 1531 | HVDC | HVDC | Khulna | BIPTC | 21T01 HT | 2023-04-15 05:20 | 2023-04-15 08:58 | 3:38 | 0 | Block-01 VCS Strainer cleaning with resin change | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
329 | 1532 | HVDC | HVDC | Khulna | BIPTC | 21T01 LT | 2023-04-15 05:20 | 2023-04-15 08:58 | 3:38 | 0 | Block-01 VCS Strainer cleaning with resin change . 511 mw power imported from India | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
330 | 11130 | HVDC | HVDC | Khulna | BIPTC | Baharampur-3 | 2023-04-01 09:52 | 2023-04-01 21:17 | 11:25 | 0 | Shutdown is taken from Berhampore substation for maintenance work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
331 | 11130 | HVDC | HVDC | Khulna | BIPTC | Baharampur-3 | 2023-04-02 10:04 | 2023-04-02 21:02 | 10:58 | 0 | Shutdown is taken from Berhampore substation end for maintenance work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
332 | 11131 | HVDC | HVDC | Khulna | BIPTC | Baharampur-4 | 2023-04-03 10:11 | 2023-04-03 20:02 | 9:51 | 0 | shutdown is taken from baharampur end at 10:11 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
333 | 11131 | HVDC | HVDC | Khulna | BIPTC | Baharampur-4 | 2023-04-04 10:03 | 2023-04-04 20:03 | 10:00 | 0 | Shutdown is taken from Baharampur S/S end at 10:03 BST | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
334 | 11131 | HVDC | HVDC | Khulna | BIPTC | Baharampur-4 | 2023-04-05 10:04 | 2023-04-05 21:40 | 11:36 | 0 | Shutdown is taken from baharampur s/s end | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
335 | 11131 | HVDC | HVDC | Khulna | BIPTC | Baharampur-4 | 2023-04-06 10:00 | 2023-04-06 20:01 | 10:01 | 0 | 400 kv Baharampur ckt-4 shutdown at baharampur end | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
336 | 2618 | HVDC | Ishurdi | Rajshahi | Baghabari 230/132kV Grid Sub-Station | Bus-2 | 2023-04-08 11:00 | 2023-04-08 11:55 | 0:55 | 0 | Ruppur line project work(Riser conductor Measurement) | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0
337 | 1890 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2023-04-13 17:50 | 2023-04-14 04:35 | 10:45 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
338 | 1908 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
339 | 1908 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 2023-04-18 11:02 | 2023-04-18 12:51 | 1:49 | 0 | Red hot Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
340 | 1932 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-04-13 17:50 | 2023-04-13 18:26 | 0:36 | 1 | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
341 | 1932 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-04-19 09:33 | 2023-04-19 10:44 | 1:11 | 0 | for tighting work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
342 | 1933 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-04-13 17:50 | 2023-04-13 18:26 | 0:36 | 1 | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
343 | 1972 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Pabna | 2023-04-13 17:50 | 2023-04-14 05:03 | 11:13 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 92 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
344 | 2744 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | 1 | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 30 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
345 | 2744 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-04-19 10:54 | 2023-04-19 11:30 | 0:36 | 0 | Red hot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
346 | 2745 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | 1 | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 30 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
347 | 2757 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2023-04-13 17:50 | 2023-04-14 04:51 | 11:01 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 20 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
348 | 2767 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -1 | 2023-04-13 17:50 | 2023-04-14 04:45 | 10:55 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 65 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
349 | 2779 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -2 | 2023-04-13 17:51 | 2023-04-13 18:24 | 0:33 | 1 | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 65 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
350 | 2803 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-1 | 2023-04-13 17:50 | 2023-04-13 18:33 | 0:43 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
351 | 2810 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-2 | 2023-04-13 17:50 | 2023-04-14 04:53 | 11:03 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
352 | 2864 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2023-04-13 17:50 | 2023-04-14 04:40 | 10:50 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 60 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
353 | 2867 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2023-04-13 17:50 | 2023-04-14 04:40 | 10:50 | 1 | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 60 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
354 | 2867 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2023-04-24 19:12 | 2023-04-24 19:23 | 0:11 | 1 | C PHASE TO GROUND FAULT | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
355 | 2653 | HVDC | Ishurdi | Rajshahi | Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 HT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | 1 | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
356 | 2654 | HVDC | Ishurdi | Rajshahi | Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 LT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | 1 | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
357 | 8416 | HVDC | Ishurdi | Rajshahi | Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2023-04-13 17:50 | 2023-04-14 04:35 | 10:45 | 1 | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
358 | 8417 | HVDC | Ishurdi | Rajshahi | Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 LT | 2023-04-13 17:50 | 2023-04-14 04:35 | 10:45 | 1 | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
359 | 4306 | HVDC | Ishurdi | Rajshahi | Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-04-16 08:16 | 2023-04-16 11:20 | 3:04 | 0 | Shahjadpur- Bhagabari 71 ckt 132 Kv ckt (Red hot) | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
360 | 3714 | HVDC | Ishurdi | Rajshahi | Ruppur 132/11kV Grid Sub-Station | TR-01 HT | 2023-04-04 13:23 | 2023-04-04 14:41 | 1:18 | 0 | 11kv annual maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
361 | 3715 | HVDC | Ishurdi | Rajshahi | Ruppur 132/11kV Grid Sub-Station | TR-01 LT | 2023-04-13 17:54 | 2023-04-13 18:40 | 0:46 | 0 | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
362 | 3732 | HVDC | Ishurdi | Rajshahi | Ruppur 132/11kV Grid Sub-Station | TR-02 HT | 2023-04-04 10:42 | 2023-04-04 13:09 | 2:27 | 0 | 11kv annual maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
363 | 3827 | HVDC | Ishurdi | Rajshahi | Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-1 | 2023-04-13 17:48 | 2023-04-13 18:35 | 0:47 | 1 | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 2.5 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
364 | 3830 | HVDC | Ishurdi | Rajshahi | Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-2 | 2023-04-13 17:48 | 2023-04-14 04:52 | 11:04 | 1 | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 2.5 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
365 | 3958 | HVDC | Ishurdi | Rajshahi | Ruppur 132/11kV Grid Sub-Station | AUX Tr-01 LT | 2023-04-13 17:48 | 2023-04-13 18:36 | 0:48 | 1 | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
366 | 9759 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-04-12 19:56 | 2023-04-12 21:16 | 1:20 | 0 | 132 kV CT Red-Hot (Y-Phase) maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
367 | 10711 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2023-04-05 10:59 | 2023-04-05 11:59 | 1:00 | 0 | Redhot Maintenance for R-phase LT Bosing side. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
368 | 10711 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2023-04-07 10:40 | 2023-04-07 12:35 | 1:55 | 0 | 132 kV Buss DS (421, Y-Phase) Red-hot Maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
369 | 10712 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) LT | 2023-04-04 13:12 | 2023-04-04 14:35 | 1:23 | 0 | Red hot | 22 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
370 | 10712 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) LT | 2023-04-06 22:27 | 2023-04-07 17:35 | 19:08 | 0 | Redhot | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
371 | 10713 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2023-04-17 10:27 | 2023-04-17 11:59 | 1:32 | 0 | 33 kV T-4 Incoming DS (B-Phase) Red-hot Maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
372 | 10714 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-04-25 15:10 | 2023-04-25 16:32 | 1:22 | 0 | PBS outgoing Feeder Emergency Maintenance | 15 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
373 | 3770 | HVDC | Jhenaidah | Khulna | Bheramara 230/132kV Grid Sub-Station | Transformer-2 HT | 2023-04-01 07:44 | 2023-04-03 12:30 | 52:46 | 0 | Aircell change | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
374 | 3771 | HVDC | Jhenaidah | Khulna | Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2023-04-01 07:44 | 2023-04-03 12:30 | 52:46 | 0 | Aircell change | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
375 | 4110 | HVDC | Jhenaidah | Khulna | Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-04-13 17:49 | 2023-04-14 04:48 | 10:59 | 1 | O/C | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
376 | 7558 | HVDC | Jhenaidah | Khulna | Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2023-04-13 17:49 | 2023-04-14 04:48 | 10:59 | 1 | O/C | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
377 | 1638 | HVDC | Jhenaidah | Khulna | Bheramara(GK) 132/33kV Grid Sub-Station | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-1 | 2023-04-19 10:18 | 2023-04-19 12:06 | 1:48 | 0 | Line Ckt-1 Line DS B phase redhot | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
378 | 1965 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | T-1 HT | 2023-04-07 07:15 | 2023-04-07 10:22 | 3:07 | 0 | red hot maintainence | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
379 | 1965 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | T-1 HT | 2023-04-15 08:09 | 2023-04-15 10:18 | 2:09 | 0 | T1 transformer red hot maintainence | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
380 | 1966 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-04-07 07:14 | 2023-04-07 10:23 | 3:09 | 0 | red hot maintainence | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
381 | 1966 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-04-15 08:08 | 2023-04-15 10:18 | 2:10 | 0 | T1 transformer red hot maintainence | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
382 | 2294 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | T-2 HT | 2023-04-15 06:10 | 2023-04-15 07:50 | 1:40 | 0 | T2A 33 kv side Hot spot maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
383 | 2295 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | T-2 LT | 2023-04-15 06:10 | 2023-04-15 07:51 | 1:41 | 0 | T2A 33 kv side Hot spot maintenance | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
384 | 5463 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-04-10 13:51 | 2023-04-10 15:20 | 1:29 | 1 | earth fault | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
385 | 5466 | HVDC | Jhenaidah | Khulna | Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2023-04-10 13:51 | 2023-04-10 15:20 | 1:29 | 1 | overcurrent | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
386 | 2697 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-04-13 10:59 | 2023-04-13 13:25 | 2:26 | 0 | 33kv T1A incommer B-Phase Rad hot Maintenance. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
387 | 2697 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-04-18 07:21 | 2023-04-18 09:02 | 1:41 | 0 | Red hot maintenance | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
388 | 2698 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-04-13 10:58 | 2023-04-13 13:26 | 2:28 | 0 | 33kv T1A incommer B-Phase Rad hot Maintenance. | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
389 | 2698 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-04-18 07:21 | 2023-04-18 09:02 | 1:41 | 0 | Red hot maintenance | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
390 | 2698 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-04-24 15:10 | 2023-04-24 15:47 | 0:37 | 1 | 33 pbs feeder loop Y phase disconnect | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
391 | 2701 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 LT | 2023-04-24 15:10 | 2023-04-24 15:47 | 0:37 | 1 | 33 kv pbs feeder Y phase Disconnect | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
392 | 11695 | HVDC | Jhenaidah | Khulna | Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-04-13 20:07 | 2023-04-14 05:38 | 9:31 | 0 | Instruction of ALDC | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
393 | 11695 | HVDC | Jhenaidah | Khulna | Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-04-19 19:28 | 2023-04-19 23:49 | 4:21 | 0 | Instruction of ALDC | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
394 | 1936 | HVDC | Jhenaidah | Khulna | Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2023-04-19 12:35 | 2023-04-19 12:58 | 0:23 | 1 | Winding Temp high | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
395 | 1937 | HVDC | Jhenaidah | Khulna | Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2023-04-19 12:35 | 2023-04-19 13:00 | 0:25 | 1 | Inter Trip From 132KV TR FDR | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
396 | 2916 | HVDC | Jhenaidah | Khulna | Magura 132/33kV Grid Sub-Station | Narail Ckt. - 1 | 2023-04-11 10:11 | 2023-04-11 16:58 | 6:47 | 0 | Work for Narail Sub-Station. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
397 | 6725 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-04-17 08:15 | 2023-04-17 08:43 | 0:28 | 0 | Red-hot remove at 33kv Jhalokathi feeder. | 22 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
398 | 6726 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-04-17 07:15 | 2023-04-17 08:43 | 1:28 | 0 | Red-hot remove at 33kv Jhalokathi feeder. | 22 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
399 | 6743 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-04-12 09:22 | 2023-04-12 10:27 | 1:05 | 0 | Removal red hot of 33 kV side Y phase CT | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
400 | 6743 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-04-18 05:38 | 2023-04-18 06:53 | 1:15 | 0 | Hot spot tightening work. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
401 | 6744 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-04-12 09:23 | 2023-04-12 10:28 | 1:05 | 0 | Removal red hot of 33 kV side Y phase CT | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
402 | 6744 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-04-18 05:37 | 2023-04-18 06:54 | 1:17 | 0 | Hot spot tightening work. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
403 | 7114 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-4 HT | 2023-04-18 07:26 | 2023-04-18 12:51 | 5:25 | 0 | Red Hot Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
404 | 7114 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-4 HT | 2023-04-21 08:02 | 2023-04-21 12:10 | 4:08 | 0 | Red hot maintenance of 33 kv side | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
405 | 7115 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-04-18 07:25 | 2023-04-18 12:53 | 5:28 | 0 | Red Hot Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
406 | 7115 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-04-21 08:01 | 2023-04-21 12:13 | 4:12 | 0 | Red hot maintenance of 33 side if T4 transformer. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
407 | 7120 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-08 11:55 | 2023-04-08 12:25 | 0:30 | 0 | 33kv isolator maintenance of Jalokathi | 16 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
408 | 7120 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-15 07:26 | 2023-04-15 10:45 | 3:19 | 0 | Red Hot Maintenance at 33 kv Bus DS | 22 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
409 | 7120 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-19 08:14 | 2023-04-19 12:35 | 4:21 | 0 | Red hot maintence | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
410 | 7120 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-20 08:33 | 2023-04-20 11:12 | 2:39 | 0 | 33kv DS maintenance of jhalokathi PBS | 26 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
411 | 7121 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-08 11:54 | 2023-04-08 12:28 | 0:34 | 0 | 33kv isolator maintenance of Jhalokathi feeder. | 16 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
412 | 7121 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-15 07:25 | 2023-04-15 10:48 | 3:23 | 0 | Red Hot Maintenance at 33 kv BUS DS | 22 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
413 | 7121 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-19 08:13 | 2023-04-19 12:37 | 4:24 | 0 | Red hot maintence | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
414 | 7121 | Khulna | Barisal | Barishal | Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-20 09:32 | 2023-04-20 11:13 | 1:41 | 0 | 33kv DS maintenance of Jhalokathi PBS | 26 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
415 | 3806 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2023-04-10 07:26 | 2023-04-10 09:27 | 2:01 | 0 | None | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
416 | 12005 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-1 | 2023-04-06 07:15 | 2023-04-06 09:56 | 2:41 | 0 | Aminbazer work | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0
417 | 12006 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-2 | 2023-04-09 07:36 | 2023-04-09 12:25 | 4:49 | 0 | Aminbazar 400kv ss side Project work | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
418 | 12008 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-04-10 12:04 | 2023-04-10 12:48 | 0:44 | 0 | Hot spot maintenance | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
419 | 12009 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2023-04-10 11:22 | 2023-04-10 12:02 | 0:40 | 0 | Hot spot maintenance | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
420 | 12015 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-2 | 2023-04-10 07:32 | 2023-04-10 09:27 | 1:55 | 0 | None | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
421 | 9048 | Khulna | Faridpur | Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2023-04-10 12:05 | 2023-04-10 12:48 | 0:43 | 0 | Ins by aldc | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
422 | 9048 | Khulna | Faridpur | Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2023-04-19 09:06 | 2023-04-19 12:59 | 3:53 | 0 | High Temperature Maintenance | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
423 | 9049 | Khulna | Faridpur | Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-02 | 2023-04-10 11:23 | 2023-04-10 12:03 | 0:40 | 0 | Instructions by Aldc | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
424 | 9049 | Khulna | Faridpur | Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-02 | 2023-04-19 09:12 | 2023-04-19 14:00 | 4:48 | 0 | High Temperature Maintenance | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
425 | 2576 | Khulna | Khulna (N) | Khulna | Goalpara 132/33kV Grid Sub-Station | Bus 1 | 2023-04-11 09:55 | 2023-04-11 13:25 | 3:30 | 0 | Busbar protection relay test work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0
426 | 2693 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2023-04-25 07:02 | 2023-04-25 08:21 | 1:19 | 0 | Transformer oil leakage | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
427 | 2694 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-04-25 07:01 | 2023-04-25 08:22 | 1:21 | 0 | Transformer oil leakage. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
428 | 4526 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-04-05 08:07 | 2023-04-05 09:25 | 1:18 | 0 | SF6 Gas Leakage Maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
429 | 4526 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-04-13 07:25 | 2023-04-13 11:21 | 3:56 | 0 | For Gas leakage of B phase | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
430 | 4526 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-04-15 07:10 | 2023-04-15 12:16 | 5:06 | 0 | SF6 gas leakage maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
431 | 4527 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-04-05 08:06 | 2023-04-05 09:27 | 1:21 | 0 | SF6 Gas Leakage Maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
432 | 4527 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-04-13 07:25 | 2023-04-13 11:22 | 3:57 | 0 | For SF6 Gas leakage of B Phase | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
433 | 4527 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-04-15 07:10 | 2023-04-15 12:17 | 5:07 | 0 | SF6 gas leakage maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
434 | 4757 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- Noapara-2 | 2023-04-02 12:39 | 2023-04-02 13:16 | 0:37 | 1 | Not indentify | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
435 | 4776 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2023-04-12 23:48 | 2023-04-13 01:22 | 1:34 | 0 | For temperature reduced | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
436 | 4923 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | TR1 (403-T) HT | 2023-04-11 10:08 | 2023-04-11 17:05 | 6:57 | 0 | New 132 KV bus connection with existing 132KV bus,and red hot maintenance work at 33KV incomer-01 TR-01 side DS. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
437 | 4924 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-04-11 10:10 | 2023-04-11 17:07 | 6:57 | 0 | New 132 KV Bus connection with Existing 132KV Bus and red hot maintenance work at 33 KV incomer -01, tr-01 side DS. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
438 | 5261 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | Magura 1 | 2023-04-11 10:08 | 2023-04-11 16:45 | 6:37 | 0 | New 132 KV Bus connection with Existing 132KV Bus and red hot maintenance work at 33 KV incomer -01, tr-01 side DS. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
439 | 1538 | Khulna | Khulna (N) | Khulna | Noapara 132/33kV Grid Sub-Station | Jashore-1 | 2023-04-10 13:52 | 2023-04-10 15:22 | 1:30 | 1 | Distance Relay Fault | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
440 | 4363 | Khulna | Khulna (N) | Khulna | Noapara 132/33kV Grid Sub-Station | khulna central - 2 | 2023-04-02 12:39 | 2023-04-02 13:16 | 0:37 | 1 | Distance Relay Tripping | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
441 | 3750 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-04-11 14:10 | 2023-04-11 14:23 | 0:13 | 1 | Over current Earth fault for 33kv pirojpur WPDCL feeder. | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
442 | 3750 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-04-12 10:10 | 2023-04-12 10:20 | 0:10 | 1 | Pirozput WZPDCl feeder fault. | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
443 | 3785 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) HT | 2023-04-11 14:10 | 2023-04-11 14:23 | 0:13 | 1 | Over current Earth fault for 33kv pirojpur WPDCL feeder. | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
444 | 3785 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) HT | 2023-04-12 10:10 | 2023-04-12 10:23 | 0:13 | 1 | Pirozpur WZPDCL feeder fault. | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
445 | 3786 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-04-11 14:10 | 2023-04-11 14:24 | 0:14 | 1 | Over current Earth fault for 33kv pirojpur WPDCL feeder. | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
446 | 3786 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-04-12 10:10 | 2023-04-12 10:24 | 0:14 | 1 | Pirozput WZPDCl feeder fault. | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
447 | 5089 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) HT | 2023-04-06 07:18 | 2023-04-06 09:01 | 1:43 | 0 | 33KV Bus Section -03 Shut Down. | 25 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
448 | 5090 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2023-04-06 07:17 | 2023-04-06 09:02 | 1:45 | 0 | 33KV Bus Section -03 Shut Down. | 25 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0
449 | 11887 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-04-04 10:12 | 2023-04-04 12:28 | 2:16 | 0 | SCADA Operation work by BPDB,Khulna. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
450 | 11887 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-04-04 13:25 | 2023-04-04 14:15 | 0:50 | 0 | SCADA work by BPDB,Khulna. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
451 | 11887 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-04-17 09:36 | 2023-04-17 12:16 | 2:40 | 0 | SCADA test by BPDB | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0
452 | 1529 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 HT | 2023-04-23 14:17 | 2023-04-23 17:33 | 3:16 | 0 | 33 KV R & Y Phase CT Oil Leakage. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
453 | 1530 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-04-23 14:16 | 2023-04-23 17:35 | 3:19 | 0 | 33 KV R & Y Phase CT Oil Leakage. | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
454 | 1530 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-04-24 18:48 | 2023-04-24 19:51 | 1:03 | 1 | 33 kv BICL feeder fault | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
455 | 5366 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-2 HT | 2023-04-06 08:21 | 2023-04-12 22:33 | 158:12 | 0 | Project work | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
456 | 5367 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-04-06 08:20 | 2023-04-12 22:34 | 158:14 | 0 | Project work | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0
457 | 5367 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-04-24 18:48 | 2023-04-24 20:14 | 1:26 | 1 | 33 kv BICL feeder fault | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
458 | 2657 | Khulna | Khulna (S) | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2023-04-01 22:21 | 2023-04-01 23:40 | 1:19 | 0 | Due to red hot at 33 KV kalaroa feeder | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
459 | 2658 | Khulna | Khulna (S) | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2023-04-01 22:21 | 2023-04-01 23:42 | 1:21 | 0 | Due to red hot at 33 KV kalaroa feeder | 55 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0
460 | 2658 | Khulna | Khulna (S) | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2023-04-17 21:22 | 2023-04-17 21:39 | 0:17 | 1 | Over current | 155 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
461 | 2678 | Khulna | Khulna (S) | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2023-04-17 21:22 | 2023-04-17 21:39 | 0:17 | 1 | Definite over current | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
462 | 2679 | Khulna | Khulna (S) | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-04-17 21:22 | 2023-04-17 22:12 | 0:50 | 1 | Due to over current | 65.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0