## Sheet1
| outage_time | eq_id | circle | gmd | zone | substation | equipment | is_bus | is_transformer | is_line | event_info | is_trip | is_scheduled | is_forced | is_project_work | outage_status_sum | is_restored | mw_interruption | restoration_time | duration
0 | 2022-02-24 16:05 | 7816 | Bogura | Rajshahi | Rajshahi | Niamatpur 132/33kV Grid Sub-Station | 407T HT | 0 | 1 | 0 | T-1 33kV bus -à¦à¦° sky wire à¦›à¦¿à¦°à§‡ à§Ÿà¦¾à¦“à§Ÿà¦¾à¦‡ forced Shut Down à¦¨à§‡à¦“à§Ÿà¦¾ à¦¹à§Ÿà¥¤ | 0 | 0 | 1 | 0 | 1 | 0 | 15 | 2022-02-24 17:07 | 0.043056
1 | 2022-02-24 16:05 | 7817 | Bogura | Rajshahi | Rajshahi | Niamatpur 132/33kV Grid Sub-Station | 407T LT | 0 | 1 | 0 | T-1 33kV bus -à¦à¦° sky wire à¦›à¦¿à¦°à§‡ à§Ÿà¦¾à¦“à§Ÿà¦¾à¦‡ forced Shut Down à¦¨à§‡à¦“à§Ÿà¦¾ à¦¹à§Ÿà¥¤ | 0 | 0 | 1 | 0 | 1 | 0 | 15 | 2022-02-24 17:07 | 0.043056
2 | 2022-02-24 06:39 | 2656 | Bogura | Rajshahi | Rajshahi | Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 0 | 1 | 0 | Due to Maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 08:43 | 0.086111
3 | 2022-02-23 09:05 | 2712 | Chattogram | Chattogram (Central) | Chattogram | Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 0 | 0 | 1 | Annual Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 13:31 | 0.18472
4 | 2022-02-25 10:02 | 2961 | Chattogram | Chattogram (Central) | Chattogram | Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 0 | 1 | 0 | Due to red hot at CT clamp R-phase. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 10:32 | 0.020833
5 | 2022-02-25 10:02 | 2962 | Chattogram | Chattogram (Central) | Chattogram | Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) LT | 0 | 1 | 0 | Due to red hot at Ct clamp R-phase. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 10:40 | 0.026389
6 | 2022-02-26 08:41 | 1973 | Chattogram | Chattogram (Central) | Chattogram | Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 0 | 0 | 1 | annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-26 12:30 | 0.15903
7 | 2022-02-27 08:17 | 6817 | Chattogram | Chattogram (Central) | Chattogram | Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 0 | 0 | 1 | S/D For Annual Maintenance at Julda Grid S/S | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 14:34 | 0.26181
8 | 2022-02-28 07:39 | 6821 | Chattogram | Chattogram (Central) | Chattogram | Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 0 | 0 | 1 | Annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 12:24 | 0.19792
9 | 2022-02-23 08:17 | 3765 | Chattogram | Chattogram (North) | Chattogram | Rangamati 132/33kV Grid Sub-Station | Power Transformer TR2 (415T) HT | 0 | 1 | 0 | Annual Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 16:42 | 0.35069
10 | 2022-02-23 08:16 | 3766 | Chattogram | Chattogram (North) | Chattogram | Rangamati 132/33kV Grid Sub-Station | Power Transformer TR2 (415T) LT | 0 | 1 | 0 | Annual Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 16:54 | 0.35972
11 | 2022-02-26 08:17 | 9631 | Cumilla | Cumilla | Cumilla | Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 0 | 0 | 1 | Annual maintenance work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-26 16:57 | 0.36111
12 | 2022-02-27 08:31 | 9632 | Cumilla | Cumilla | Cumilla | Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 0 | 0 | 1 | Annual Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:15 | 0.36389
13 | 2022-02-25 06:56 | 3145 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | Feni-1 | 0 | 0 | 1 | annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 12:51 | 0.24653
14 | 2022-02-25 07:15 | 3149 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 0 | 0 | 1 | annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 13:52 | 0.27569
15 | 2022-02-27 08:22 | 3149 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 0 | 0 | 1 | Annual Maintenance Works. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 15:35 | 0.30069
16 | 2022-02-24 07:54 | 5066 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 0 | 0 | 1 | bus maintenance ashuganj end | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 08:28 | 0.023611
17 | 2022-02-23 09:20 | 5072 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 0 | 0 | 1 | Annual maintenance purpose | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 16:24 | 0.29444
18 | 2022-02-24 09:42 | 1520 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-1 HT | 0 | 1 | 0 | ten delta test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 14:19 | 0.19236
19 | 2022-02-24 09:41 | 1521 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 0 | 1 | 0 | ten delta test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 14:19 | 0.19306
20 | 2022-02-25 06:50 | 1688 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | Bus-1 | 1 | 0 | 0 | AMS-2021-22 & New Bus DS Install work | 0 | 1 | 0 | 0 | 1 | 0 | 27 | 2022-02-25 12:52 | 0.25139
21 | 2022-02-25 07:14 | 1689 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | Bus-2 | 1 | 0 | 0 | AMS-2021-22 & New Bus DS Installation | 0 | 1 | 0 | 0 | 1 | 0 | 27 | 2022-02-25 13:02 | 0.24167
22 | 2022-02-28 12:49 | 1740 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 0 | 1 | 0 | Tendelta Test (AMS-2021-22) | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 16:20 | 0.14653
23 | 2022-02-28 08:30 | 1742 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 0 | 1 | 0 | Ten Delta Test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 12:48 | 0.17917
24 | 2022-02-23 10:59 | 11279 | Cumilla | Srimongol | Sylhet | Bibiana 400/230kV Sub-Station | Bibiyana-III GTG | 0 | 0 | 1 | Bibiyana -3 x-former maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 16:05 | 1.2125
25 | 2022-02-26 11:38 | 11280 | Cumilla | Srimongol | Sylhet | Bibiana 400/230kV Sub-Station | Bibiyana-III STG | 0 | 0 | 1 | Bibiyana-3 ( STG) Generations Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 16:44 | 2.2125
26 | 2022-02-23 09:17 | 7705 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 0 | 1 | 0 | hot spot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-23 10:30 | 0.050694
27 | 2022-02-23 09:17 | 7706 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 0 | 1 | 0 | hot spot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-23 10:30 | 0.050694
28 | 2022-02-24 09:22 | 9285 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 0 | 0 | 1 | Annual maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 15:51 | 0.27014
29 | 2022-02-26 08:55 | 9285 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 0 | 0 | 1 | annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-26 17:44 | 0.36736
30 | 2022-02-27 08:47 | 9285 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 0 | 0 | 1 | Annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:56 | 0.38125
31 | 2022-02-28 08:30 | 9285 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 0 | 0 | 1 | maintenance work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 20:19 | 0.49236
32 | 2022-02-24 16:31 | 1642 | Cumilla | Sylhet | Sylhet | Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 0 | 0 | 1 | For 113-89L DC status maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-24 17:10 | 0.027083
33 | 2022-02-24 09:11 | 6772 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T1 HT | 0 | 1 | 0 | annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 14:04 | 0.20347
34 | 2022-02-25 06:10 | 6772 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T1 HT | 0 | 1 | 0 | Work on 33KV DS | 0 | 1 | 0 | 0 | 1 | 0 | 25 | 2022-02-25 10:47 | 0.19236
35 | 2022-02-27 09:21 | 3877 | Dhaka (N) | Dhaka (North) | Dhaka | Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 0 | 0 | 1 | Kodda end Project Work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-27 14:39 | 0.22083
36 | 2022-02-23 08:28 | 281 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) HT | 0 | 1 | 0 | Tan Delta Test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 12:57 | 0.18681
37 | 2022-02-23 08:28 | 282 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) LT | 0 | 1 | 0 | Tan Delta Test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 12:57 | 0.18681
38 | 2022-02-23 13:17 | 283 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) HT | 0 | 1 | 0 | Tan Delta Test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 16:43 | 0.14306
39 | 2022-02-24 13:01 | 283 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) HT | 0 | 1 | 0 | Tap Changer PRV False Trip | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 15:51 | 0.11806
40 | 2022-02-23 13:17 | 284 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 0 | 1 | 0 | Tan Delta Test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 16:53 | 0.15
41 | 2022-02-24 13:01 | 284 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 0 | 1 | 0 | Tap Changer PRV False Trip | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 15:51 | 0.11806
42 | 2022-02-26 07:31 | 292 | Dhaka (N) | Dhaka(North-West) | Dhaka | Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 0 | 0 | 1 | Dead line checking | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-26 15:41 | 0.34028
43 | 2022-02-28 07:28 | 1105 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | Reserve bus | 1 | 0 | 0 | Insulator replacement work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 17:32 | 0.41944
44 | 2022-02-27 08:25 | 1110 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 0 | 1 | 0 | Painting work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:01 | 0.35833
45 | 2022-02-22 07:42 | 1126 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 0 | 0 | 1 | Dead line checking | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-22 14:09 | 0.26875
46 | 2022-02-23 06:46 | 1126 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 0 | 0 | 1 | Dead Line Cheaking Work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 14:09 | 0.30764
47 | 2022-02-28 08:24 | 1127 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 0 | 0 | 1 | Dead line Checking | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 17:39 | 0.38542
48 | 2022-02-28 09:22 | 720 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | Main Bus | 1 | 0 | 0 | 132kV DS Hotspot maintenance work of T3 c-former | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 12:03 | 0.11181
49 | 2022-02-28 12:15 | 721 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 1 | 0 | 0 | 132kV DS Hotspot maintenance work of T3 c-former | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 17:57 | 0.2375
50 | 2022-02-28 09:08 | 726 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | T3 HT | 0 | 1 | 0 | 132kV DS Hotspot maintenance work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 18:01 | 0.37014
51 | 2022-02-28 09:08 | 727 | Dhaka (N) | Dhaka(North-West) | Dhaka | Mirpur 132/33kV Grid Sub-Station | T3 LT | 0 | 1 | 0 | 132kV DS Hotspot maintenance work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 18:01 | 0.37014
52 | 2022-02-23 08:25 | 24 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | oil centrifuge of t-1 transformer | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 17:39 | 1.3847
53 | 2022-02-23 08:25 | 25 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | T-1 LT | 0 | 1 | 0 | oil centrifuge of t-1 transformer | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 17:39 | 1.3847
54 | 2022-02-26 08:50 | 28 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | T-2 HT | 0 | 1 | 0 | oil cetrifuging work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:41 | 1.3687
55 | 2022-02-26 08:50 | 29 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | T-2 LT | 0 | 1 | 0 | oil centrifuging work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:41 | 1.3687
56 | 2022-02-24 06:32 | 754 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 0 | 1 | 0 | 33 kv Bus section DS maintenance of TR-1 and TR-3 | 0 | 1 | 0 | 0 | 1 | 0 | 30 | 2022-02-24 07:33 | 0.042361
57 | 2022-02-24 06:31 | 755 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | XFR, T-I LT | 0 | 1 | 0 | 33 KV Bus section DS maintenance of TR-1 and TR-3 | 0 | 1 | 0 | 0 | 1 | 0 | 30 | 2022-02-24 07:33 | 0.043056
58 | 2022-02-23 09:46 | 2003 | Dhaka (S) | Dhaka (Central) | Dhaka | Cantonment 132/33kV GIS Grid Sub-Station | Transformer-1 (T-1) HT | 0 | 1 | 0 | X-former -T1 Tan delta test. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 13:35 | 0.15903
59 | 2022-02-23 09:45 | 2004 | Dhaka (S) | Dhaka (Central) | Dhaka | Cantonment 132/33kV GIS Grid Sub-Station | Transformer-1 (T-1) LT | 0 | 1 | 0 | X-former -T1 Tan delta test. Operated by DESCO | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 13:35 | 0.15972
60 | 2022-02-23 13:50 | 2105 | Dhaka (S) | Dhaka (Central) | Dhaka | Cantonment 132/33kV GIS Grid Sub-Station | Transformer-2 (T-2) HT | 0 | 1 | 0 | X-former -T2 Tan delta test. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 15:07 | 0.053472
61 | 2022-02-23 13:50 | 2106 | Dhaka (S) | Dhaka (Central) | Dhaka | Cantonment 132/33kV GIS Grid Sub-Station | Transformer-2 (T-2) LT | 0 | 1 | 0 | X-former -T2 Tan delta test. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 15:07 | 0.053472
62 | 2022-02-23 09:16 | 1813 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 0 | 0 | 1 | Narinda End X-former oil leak Maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 17:44 | 0.35278
63 | 2022-02-25 11:34 | 2728 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 0 | 0 | 1 | à¦•à¦¾à¦œà¦²à¦¾ à¦¸à¦¾à¦°à§à¦•à¦¿à¦Ÿ-à§¦à§§ à¦à¦° R-à¦«à§‡à¦œà§‡à¦° à¦²à¦¾à¦‡à¦Ÿà¦¨à¦¿à¦‚ à¦à¦°à§‡à¦¸à§à¦Ÿà¦° à¦ªà¦°à¦¿à¦¬à¦°à§à¦¤à¦¨à§‡à¦° à¦œà¦¨à§à¦¯ à¦œà¦¨à¦¾à¦¬ à¦¸à¦¾à¦‡à¦¦ à¦®à¦¾à¦¹à¦®à§à¦¦,SAE,DPDC à¦¶à¦¾à¦Ÿ à¦¡à¦¾à¦‰à¦¨ à¦¨à§‡à¦¨à¥¤ | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 14:27 | 0.12014
64 | 2022-02-23 09:58 | 1437 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 1 | 0 | 0 | S/D for Dhaka University Bay connection in 132kv Bus-1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-23 19:40 | 0.40417
65 | 2022-02-24 10:09 | 1438 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 1 | 0 | 0 | S/D for Dhaka University Bay connection in 132kv Bus-2 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-24 17:26 | 0.30347
66 | 2022-02-28 09:38 | 3280 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 0 | 0 | 1 | Line Fault | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 15:24 | 0.24028
67 | 2022-02-25 08:48 | 7622 | Dhaka (S) | Dhaka (East) | Dhaka | Madanganj 132/33kV Grid Sub-Station | GT-2 HT | 0 | 1 | 0 | Annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 18:03 | 0.38542
68 | 2022-02-25 08:42 | 7623 | Dhaka (S) | Dhaka (East) | Dhaka | Madanganj 132/33kV Grid Sub-Station | GT-2 LT | 0 | 1 | 0 | Annual maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-25 18:07 | 0.39236
69 | 2022-02-25 09:10 | 1948 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | T-2 HT | 0 | 1 | 0 | Corrective maintenance work done by DPDC | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-25 12:37 | 0.14375
70 | 2022-02-25 09:15 | 1949 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | T-2 LT | 0 | 1 | 0 | Corrective maintenance work done by DPDC | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-25 12:42 | 0.14375
71 | 2022-02-23 08:36 | 2359 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 0 | 0 | 1 | Annual maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 13:34 | 0.20694
72 | 2022-02-24 09:30 | 2359 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 0 | 0 | 1 | Annual Maintenance @ Siddhirganj ss end | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 11:58 | 0.10278
73 | 2022-02-28 09:08 | 2362 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 0 | 0 | 1 | Annual Maintenances | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 13:53 | 0.19792
74 | 2022-02-28 10:45 | 5267 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Duadkandi 1 | 0 | 0 | 1 | Daudkandi Ckt - 01, R phase spring charge motor problem. Motor to be changed. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-28 11:40 | 0.038194
75 | 2022-02-24 09:26 | 2664 | Dhaka (S) | Dhaka (South) | Dhaka | Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 0 | 1 | 0 | Transformer main tank topper part temperature sensor point oil leakage find out & Try to fixed . | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 17:16 | 0.32639
76 | 2022-02-27 08:20 | 6486 | Dhaka (S) | Dhaka (South) | Dhaka | Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 0 | 0 | 1 | Dead line check | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 13:20 | 0.20833
77 | 2022-02-23 10:28 | 10772 | Dhaka (S) | Dhaka (South) | Dhaka | Keranigonj 230/132/33kV Grid Sub-Station | Nawabganj-1 | 0 | 0 | 1 | Annual Maintenance Nawabganj end. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 17:29 | 0.29236
78 | 2022-02-24 09:57 | 10773 | Dhaka (S) | Dhaka (South) | Dhaka | Keranigonj 230/132/33kV Grid Sub-Station | Nawabganj-2 | 0 | 0 | 1 | Annual Maintenance at Nawabgang end | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 17:25 | 0.31111
79 | 2022-02-27 09:44 | 7748 | Dhaka (S) | Dhaka (South) | Dhaka | Nawabganj 132/33kV Grid Sub-Station | TR-1 HT | 0 | 1 | 0 | Annual Maintenance Work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:08 | 0.30833
80 | 2022-02-27 09:43 | 7749 | Dhaka (S) | Dhaka (South) | Dhaka | Nawabganj 132/33kV Grid Sub-Station | TR-1 LT | 0 | 1 | 0 | Annual Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-27 17:12 | 0.31181
81 | 2022-02-23 10:29 | 10992 | Dhaka (S) | Dhaka (South) | Dhaka | Nawabganj 132/33kV Grid Sub-Station | Keraniganj-1 | 0 | 0 | 1 | Scheduled annual maintainance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-23 17:45 | 0.30278
82 | 2022-02-24 09:56 | 10993 | Dhaka (S) | Dhaka (South) | Dhaka | Nawabganj 132/33kV Grid Sub-Station | Keraniganj-2 | 0 | 0 | 1 | Annual Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 17:05 | 0.29792
83 | 2022-02-28 09:39 | 5917 | Dhaka (S) | Narsingdi | Dhaka | Bhulta 400/230kV Grid Sub-Station | Rampura-02 | 0 | 0 | 1 | Zone 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2022-02-28 15:24 | 0.23958
84 | 2022-02-23 08:25 | 2826 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) | 0 | 0 | 1 | Project Work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-23 17:45 | 0.38889
85 | 2022-02-24 08:39 | 2826 | HVDC | Jhenaidah | Khulna | Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) | 0 | 0 | 1 | Project Work 230kV Jhenaidah ss End. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-24 10:57 | 0.095833
86 | 2022-02-24 07:41 | 6425 | Khulna | Faridpur | Khulna | Shariatpur 132/33kV Grid Sub-Station | 33 KV BUS | 1 | 0 | 0 | 33 KV Bus section-2 maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 11:15 | 0.14861
87 | 2022-02-24 07:46 | 6666 | Khulna | Faridpur | Khulna | Shariatpur 132/33kV Grid Sub-Station | T2-416T HT | 0 | 1 | 0 | 33 KV Bus section-2 maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 11:15 | 0.14514
88 | 2022-02-24 07:45 | 6667 | Khulna | Faridpur | Khulna | Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 0 | 1 | 0 | 33 KV Bus section-2 maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2022-02-24 11:13 | 0.14444
89 | 2022-02-24 00:22 | 10284 | Khulna | Khulna (S) | Khulna | Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 0 | 0 | 1 | Order by SAE ALDC, Khulna. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-24 07:28 | 0.29583
90 | 2022-02-26 03:05 | 10284 | Khulna | Khulna (S) | Khulna | Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 0 | 0 | 1 | Order by ALDC, Khulna. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-26 08:13 | 0.21389
91 | 2022-02-28 00:12 | 10284 | Khulna | Khulna (S) | Khulna | Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 0 | 0 | 1 | order by ALDC, Khulna. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2022-02-28 07:18 | 0.29583
92 | 2022-02-25 09:39 | 3661 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 1 | 0 | 0 | 230 kV Main Bus-1 Shutdown for PDB Project Work (Bus Connection. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-25 16:40 | 0.29236
93 | 2022-02-26 09:32 | 3666 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 1 | 0 | 0 | 230 kV main Bus-2 Shutdown for PDB Project Work (Bus Connection). | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-26 13:44 | 0.175
94 | 2022-02-25 08:19 | 4025 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | Jhenaidah Ckt-1 | 0 | 0 | 1 | 230 kV Jhenaidah Ckt-1 Shutdown for Project Work in jhenaidah SS. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-25 17:48 | 0.39514
95 | 2022-02-26 08:55 | 4025 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | Jhenaidah Ckt-1 | 0 | 0 | 1 | 230 kV main Bus-2 Shutdown for PDB Project Work (Bus Connection). | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-26 14:35 | 0.23611
96 | 2022-02-25 08:21 | 4138 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | Jhenaidah Ckt-2 | 0 | 0 | 1 | 230 kV Jhenaidah Ckt-2 Shutdown for Project Work in jhenaidah SS. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2022-02-25 18:02 | 0.40347