## Sheet1
| outage_time | eq_id | circle | gmd | zone | substation | equipment | is_bus | is_transformer | is_line | event_info | is_trip | is_scheduled | is_forced | is_project_work | outage_status_sum | is_restored | mw_interruption | restoration_time | duration
0 | 2023-08-02 11:05 | 3760 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 0 | 1 | 0 | 33 kV feeder fault. | 1 | 0 | 0 | 0 | 1 | 0 | 66 | 2023-08-02 11:48 | 0.029861
1 | 2023-08-22 20:24 | 3823 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 0 | 0 | 1 | According to NLDC's instructions. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-23 17:24 | 0.875
2 | 2023-08-23 17:28 | 3823 | Bogura | Bogura | Rajshahi | Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 0 | 0 | 1 | With the permission of ALDC Bogura | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-28 08:26 | 4.6236
3 | 2023-08-24 14:20 | 6706 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | New Bogura-2 | 0 | 0 | 1 | In order by ALDC. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-24 16:44 | 0.1
4 | 2023-08-28 20:25 | 6699 | Bogura | Bogura | Rajshahi | Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 0 | 1 | 0 | Bus shift. | 0 | 0 | 1 | 0 | 1 | 0 | 34 | 2023-08-28 20:35 | 0.0069444
5 | 2023-08-07 08:50 | 7833 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 0 | 0 | 1 | Isolator arm change | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-07 11:30 | 0.11111
6 | 2023-08-11 06:07 | 7823 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | T-02 HT | 0 | 1 | 0 | Bushing conductor replacement | 0 | 1 | 0 | 0 | 1 | 0 | 143 | 2023-08-11 09:44 | 0.15069
7 | 2023-08-12 07:33 | 7832 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 0 | 0 | 1 | Red Hot Maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-12 10:10 | 0.10903
8 | 2023-08-25 06:39 | 8181 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 1 | 0 | 0 | Isolator replacement work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-25 09:48 | 0.13125
9 | 2023-08-25 15:44 | 7833 | Bogura | Bogura | Rajshahi | Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 0 | 0 | 1 | Red Hot Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-25 17:33 | 0.075694
10 | 2023-08-11 13:42 | 1946 | Bogura | Bogura | Rajshahi | Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 0 | 1 | 0 | 432B CB trip | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-11 14:14 | 0.022222
11 | 2023-08-16 22:34 | 2095 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T2-(425) HT | 0 | 1 | 0 | Emergency Red Hot Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-17 00:02 | 0.061111
12 | 2023-08-21 16:28 | 1944 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 0 | 1 | 0 | Emergency Red Hot Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-21 17:43 | 0.052083
13 | 2023-08-22 06:55 | 2320 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 0 | 0 | 1 | Conductor stringing. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-22 17:30 | 0.44097
14 | 2023-08-23 08:01 | 2320 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 0 | 0 | 1 | Sirajgonj-Sherpur- 132kV Ckt-02 conductor stringing | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-23 17:24 | 0.39097
15 | 2023-08-31 08:06 | 1944 | Bogura | Bogura | Rajshahi | Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 0 | 1 | 0 | Red Hot has become visible at 33kV T1+T2 connecting BUS Cupler DS.(This S/D has been taken By AGM com -PBS-2 and they will work on it). all operation has been conducted by the permission of XEN NLDC and according to QF -GMD-18 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-31 09:47 | 0.070139
16 | 2023-08-17 06:15 | 9382 | Bogura | Bogura | Rajshahi | Sirajgonj 230 kV Switching Station | SNWPCL (Unit-04) | 0 | 0 | 1 | Bay DS, Y Phase Red Hot detected | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-17 10:33 | 0.17917
17 | 2023-08-18 09:21 | 7696 | Bogura | Dinajpur | Rangpur | Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 0 | 1 | 0 | Red hot maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-18 11:08 | 0.074306
18 | 2023-08-28 11:20 | 6115 | Bogura | Dinajpur | Rangpur | Panchagarh 132/33kV Grid Sub-Station | 407T LT | 0 | 1 | 0 | Due to emergency maintenance in NESCO 33kV feeder bus DS. | 0 | 0 | 1 | 0 | 1 | 0 | 16 | 2023-08-28 11:55 | 0.024306
19 | 2023-08-08 07:28 | 2386 | Bogura | Rajshahi | Rajshahi | Amnura 132/33kV Grid Sub-Station | Amnura - 50MW RPP | 0 | 0 | 1 | None | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-08 22:57 | 0.64514
20 | 2023-08-05 06:51 | 11720 | Bogura | Rajshahi | Rajshahi | Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 0 | 0 | 1 | Project work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-08 20:32 | 3.5701
21 | 2023-08-24 07:46 | 9656 | Bogura | Rajshahi | Rajshahi | Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 0 | 0 | 1 | CT B phase oil leakage | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-24 13:19 | 0.23125
22 | 2023-08-29 21:25 | 9657 | Bogura | Rajshahi | Rajshahi | Chapai 132/33kV Grid Sub-Station | Chapai-Amnura | 0 | 0 | 1 | O/C | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-29 21:35 | 0.0069444
23 | 2023-08-01 18:15 | 6282 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-3 HT | 0 | 1 | 0 | Emergency red hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-01 20:15 | 0.083333
24 | 2023-08-06 00:23 | 1522 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | T-1 132 Kv CT (R-Phase) Red Hot Maintanance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-06 01:40 | 0.053472
25 | 2023-08-06 21:21 | 6283 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-3 LT | 0 | 1 | 0 | Rain fall and lightning. | 1 | 0 | 0 | 0 | 1 | 0 | 58 | 2023-08-06 21:57 | 0.025
26 | 2023-08-09 20:12 | 6275 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-2 HT | 0 | 1 | 0 | Red hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-09 20:48 | 0.025
27 | 2023-08-12 15:50 | 6276 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-2 LT | 0 | 1 | 0 | Trip | 1 | 0 | 0 | 0 | 1 | 0 | 47 | 2023-08-12 16:05 | 0.010417
28 | 2023-08-14 20:18 | 1522 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | Red hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-14 21:08 | 0.034722
29 | 2023-08-16 10:45 | 6276 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-2 LT | 0 | 1 | 0 | Heavy flashing when closing to capacitor bank-6 33 kv bus isolator. | 1 | 0 | 0 | 0 | 1 | 0 | 50 | 2023-08-16 11:05 | 0.013889
30 | 2023-08-16 11:30 | 1522 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | Showing Buchholze relay trip signal. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-16 15:10 | 0.15278
31 | 2023-08-20 08:38 | 6276 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-2 LT | 0 | 1 | 0 | Trip | 1 | 0 | 0 | 0 | 1 | 0 | 22.5 | 2023-08-20 09:13 | 0.024306
32 | 2023-08-20 15:27 | 1522 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | Mohadebpur 33 kv pbs feeder bus DS maintanance. | 0 | 0 | 1 | 0 | 1 | 0 | 30 | 2023-08-20 17:16 | 0.075694
33 | 2023-08-21 10:38 | 6275 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-2 HT | 0 | 1 | 0 | T1&T2 33KV BUS COUPLER RED HOT MAINTENANCE | 0 | 0 | 1 | 0 | 1 | 0 | 30 | 2023-08-21 12:47 | 0.089583
34 | 2023-08-24 15:54 | 6391 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 0 | 0 | 1 | Trip | 1 | 0 | 0 | 0 | 1 | 0 | 40 | 2023-08-24 16:26 | 0.022222
35 | 2023-08-31 06:55 | 1522 | Bogura | Rajshahi | Rajshahi | Naogaon 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | Red hot maintanance of mohadebpur pbs 33kvfeeder | 0 | 1 | 0 | 0 | 1 | 0 | 42 | 2023-08-31 09:18 | 0.099306
36 | 2023-08-24 07:10 | 1930 | Bogura | Rajshahi | Rajshahi | Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 0 | 1 | 0 | L.T ioop maintanance(change). | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-24 08:38 | 0.061111
37 | 2023-08-20 14:55 | 2869 | Bogura | Rajshahi | Rajshahi | Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 0 | 1 | 0 | Taherpur 33KV Natore PBS-1 Feeder Fault. (O/C, E/F) | 1 | 0 | 0 | 0 | 1 | 0 | 55 | 2023-08-20 15:10 | 0.010417
38 | 2023-08-26 12:34 | 2853 | Bogura | Rajshahi | Rajshahi | Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 0 | 1 | 0 | For Tr -2 ,HT Side CT (Y Phase) Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-26 14:28 | 0.079167
39 | 2023-08-27 16:44 | 7210 | Bogura | Rangpur | Rangpur | Jaldhaka 132/33kV Grid Sub-Station | 33 KV BUS | 1 | 0 | 0 | Bus Section-01. Red hot on the T-1 33kv Bus isolator. | 0 | 0 | 1 | 0 | 1 | 0 | 16 | 2023-08-27 18:55 | 0.090972
40 | 2023-08-10 11:39 | 3396 | Bogura | Rangpur | Rangpur | Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) HT | 0 | 1 | 0 | Tr-02 LV temperature high. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-10 13:04 | 0.059028
41 | 2023-08-08 16:30 | 7732 | Bogura | Rangpur | Rangpur | Palashbari 132/33kV Grid Sub-Station | TR1-414T HT | 0 | 1 | 0 | Red Hot. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-08 17:36 | 0.045833
42 | 2023-08-25 18:12 | 11970 | Bogura | Rangpur | Rangpur | Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 0 | 0 | 1 | DC converter Replace | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-25 21:18 | 0.12917
43 | 2023-08-29 18:45 | 3547 | Bogura | Rangpur | Rangpur | Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 0 | 0 | 1 | Suddenly Drop the Grid Voltage | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-29 19:01 | 0.011111
44 | 2023-08-31 08:09 | 3544 | Bogura | Rangpur | Rangpur | Rangpur 132/33kV Grid Sub-Station | Rangpur-Kurigram | 0 | 0 | 1 | Mohastan to Polashbari 132 KV line trip. | 1 | 0 | 0 | 0 | 1 | 0 | 62 | 2023-08-31 08:32 | 0.015972
45 | 2023-08-03 12:34 | 1961 | Chattogram | Chattogram (Central) | Chattogram | Khulshi 132/33kV Grid Sub-Station | Khulshi-AKSPL Line | 0 | 0 | 1 | CT Change & Replace in AKSPL Sub-Station. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-03 15:31 | 0.12292
46 | 2023-08-06 10:37 | 7813 | Chattogram | Chattogram (Central) | Chattogram | Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 0 | 1 | 0 | à¦…à¦•à§à¦¸à¦¿à¦²à¦¿à§Ÿà¦¾à¦°à¦¿ à¦Ÿà§à¦°à¦¾à¦¨à§à¦¸à¦«à¦°à¦®à¦¾à¦° à§©à§©/à§¦.à§ªà¦•à§‡à¦­à¦¿ à¦Ÿà¦¿-à§¦à§§ à¦¡à§à¦°à¦ª à¦†à¦‰à¦Ÿ à¦«à¦¿à¦‰à¦œ à¦ªà¦°à¦¿à¦¬à¦°à§à¦¤à¦¨ | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-06 11:37 | 0.041667
47 | 2023-08-03 12:39 | 11603 | Chattogram | Chattogram (North) | Chattogram | AKS 132/33kV Grid Sub-Station | Khulshi | 0 | 0 | 1 | BUs coupler R-phase CT oil leakage problem. this CT remove and this place new loop connection work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-03 15:30 | 0.11875
48 | 2023-08-09 15:32 | 4699 | Chattogram | Chattogram (North) | Chattogram | Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T HT | 0 | 1 | 0 | None | 0 | 0 | 1 | 0 | 1 | 0 | 21 | 2023-08-09 17:15 | 0.071528
49 | 2023-08-21 10:56 | 4699 | Chattogram | Chattogram (North) | Chattogram | Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T HT | 0 | 1 | 0 | Redhot maintenance work | 0 | 0 | 1 | 0 | 1 | 0 | 15 | 2023-08-21 12:01 | 0.045139
50 | 2023-08-31 06:51 | 4705 | Chattogram | Chattogram (North) | Chattogram | Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 0 | 0 | 1 | Line trip | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-31 13:20 | 0.27014
51 | 2023-08-01 17:50 | 2674 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 0 | 1 | 0 | 33 kV XLPE B Ph Cable Fixing | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-01 18:50 | 0.041667
52 | 2023-08-06 13:21 | 8451 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 0 | 1 | 0 | cable punture Bph | 1 | 0 | 0 | 0 | 1 | 0 | 44 | 2023-08-06 15:24 | 0.085417
53 | 2023-08-07 04:57 | 8458 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Baroaulia-02 | 0 | 0 | 1 | distance trip | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-07 05:43 | 0.031944
54 | 2023-08-07 16:50 | 8450 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | T-02 HT | 0 | 1 | 0 | Faulty cable change, | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-07 18:14 | 0.058333
55 | 2023-08-22 16:08 | 11113 | Chattogram | Chattogram (North) | Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-02 | 0 | 0 | 1 | Project work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-22 18:12 | 0.086111
56 | 2023-08-17 09:18 | 3842 | Chattogram | Chattogram (North) | Chattogram | Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-02 | 0 | 0 | 1 | Red hot. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-17 11:28 | 0.090278
57 | 2023-08-06 12:32 | 5317 | Chattogram | Chattogram (South) | Chattogram | Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 0 | 0 | 1 | Fault | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-06 16:38 | 0.17083
58 | 2023-08-13 10:09 | 5291 | Chattogram | Chattogram (South) | Chattogram | Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 0 | 1 | 0 | 33 KV bus Work | 0 | 0 | 1 | 0 | 1 | 0 | 17 | 2023-08-13 10:42 | 0.022917
59 | 2023-08-14 13:40 | 5292 | Chattogram | Chattogram (South) | Chattogram | Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 0 | 1 | 0 | 33 kv Kodala & Hosnabad feeder Trip E/F, O/C. Transformer T1 Secondary Trip by E/F, O/C. | 1 | 0 | 0 | 0 | 1 | 0 | 16 | 2023-08-14 13:53 | 0.0090278
60 | 2023-08-13 14:07 | 8826 | Chattogram | Chattogram (South) | Chattogram | Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 0 | 0 | 1 | Tree trimming | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-13 15:20 | 0.050694
61 | 2023-08-01 06:08 | 1645 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 0 | 0 | 1 | Bus coupler Bay conductor change. Doha-sik-01 is on duty. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-01 11:08 | 0.20833
62 | 2023-08-01 16:28 | 1489 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 0 | 1 | 0 | Banshkhali 33KV PBS feeder taken T-01 33KV Bus shutdown for redhot maintenance at Banshkhali 33KV PBS bus DS. | 0 | 0 | 1 | 0 | 1 | 0 | 15 | 2023-08-01 17:59 | 0.063194
63 | 2023-08-02 05:58 | 1653 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 0 | 1 | 0 | Keranihat 33 kv pbs maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 40 | 2023-08-02 07:27 | 0.061806
64 | 2023-08-13 14:10 | 1650 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 0 | 0 | 1 | SD Taken by Coxsbazar Grid | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-13 15:17 | 0.046528
65 | 2023-08-22 23:52 | 1645 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 0 | 0 | 1 | High temperance maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-23 00:54 | 0.043056
66 | 2023-08-27 14:30 | 1645 | Chattogram | Chattogram (South) | Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 0 | 0 | 1 | High Temperature maintenance of Xfer Bus DS (R) of Bus coupler Bay | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-27 15:52 | 0.056944
67 | 2023-08-16 13:28 | 5136 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 0 | 0 | 1 | General trip Zone-01,Zcom B-phase Fault | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-16 13:49 | 0.014583
68 | 2023-08-17 09:06 | 2740 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 0 | 0 | 1 | For line inspection and river-crossing conductor(Karnafully River) maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-17 16:03 | 0.28958
69 | 2023-08-18 09:51 | 2740 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 0 | 0 | 1 | For river-crossing(Karnafully river) conductor strengthening work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-18 17:23 | 0.31389
70 | 2023-08-19 08:44 | 2740 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 0 | 0 | 1 | Line inspection and maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-19 16:41 | 0.33125
71 | 2023-08-20 09:08 | 2740 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 0 | 0 | 1 | Line inspection and maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-20 16:35 | 0.31042
72 | 2023-08-30 13:21 | 2661 | Chattogram | Chattogram (South) | Chattogram | Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 0 | 1 | 0 | For Mohora-1 BPDB 33KV feeder E/F, O/C tripping | 1 | 0 | 0 | 0 | 1 | 0 | 38 | 2023-08-30 13:55 | 0.023611
73 | 2023-08-01 06:09 | 4609 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 0 | 0 | 1 | Maintenance at Dohazari S/S End | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-01 11:07 | 0.20694
74 | 2023-08-16 08:37 | 4601 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 0 | 0 | 1 | Maintenance at T.K.Chemical end | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-16 12:23 | 0.15694
75 | 2023-08-17 09:07 | 4600 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-1 | 0 | 0 | 1 | Maintenance at Madunaghat end. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-17 16:03 | 0.28889
76 | 2023-08-19 10:05 | 4620 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Interconnection-2 | 0 | 0 | 1 | Bay maintenance at Shikalbahab132KV end. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-19 12:40 | 0.10764
77 | 2023-08-20 09:07 | 4600 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-1 | 0 | 0 | 1 | Line maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-20 16:35 | 0.31111
78 | 2023-08-22 23:53 | 4609 | Chattogram | Chattogram (South) | Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 0 | 0 | 1 | High Temperature maintenance at Dohazari end. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-23 00:55 | 0.043056
79 | 2023-08-30 08:43 | 6138 | Chattogram | Chattogram (South) | Chattogram | TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) HT | 0 | 1 | 0 | red hot | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-30 09:45 | 0.043056
80 | 2023-08-12 11:54 | 9623 | Cumilla | Cumilla | Cumilla | Chandpur 132/33kV Grid Sub-Station | Bus-B | 1 | 0 | 0 | Bus pt glass broken | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-12 15:53 | 0.16597
81 | 2023-08-17 15:39 | 3149 | Cumilla | Cumilla | Cumilla | Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 0 | 0 | 1 | Line to ground fault. | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-17 19:35 | 0.16389
82 | 2023-08-01 11:30 | 4450 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | HFPL line | 0 | 0 | 1 | Tripped | 1 | 0 | 0 | 0 | 1 | 0 | 56 | 2023-08-03 16:38 | 2.2139
83 | 2023-08-05 11:56 | 4426 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 0 | 0 | 1 | Emergency tree trimming. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-05 12:50 | 0.0375
84 | 2023-08-06 16:06 | 4383 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | TR3-435T LT | 0 | 1 | 0 | 33 KV Datterhat feeder O/C E/F Trip | 1 | 0 | 0 | 0 | 1 | 0 | 25 | 2023-08-06 16:12 | 0.0041667
85 | 2023-08-07 15:12 | 4387 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | TR3 | 1 | 0 | 0 | T-3 Bus S/D for Chow-T-3 bus Isolator red hot maintenance by BPDB. | 0 | 0 | 1 | 0 | 1 | 0 | 30 | 2023-08-07 16:10 | 0.040278
86 | 2023-08-10 06:38 | 4418 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 0 | 0 | 1 | Line Jumper Open Y phase | 1 | 0 | 0 | 0 | 1 | 0 | 20 | 2023-08-10 07:00 | 0.015278
87 | 2023-08-10 07:01 | 4418 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 0 | 0 | 1 | Line Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-10 19:23 | 0.51528
88 | 2023-08-13 07:10 | 4385 | Cumilla | Cumilla | Cumilla | Chowmuhani 132/33kV Grid Sub-Station | TR1 | 1 | 0 | 0 | 33 kV Maizdee feeder bus isolator red hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 30 | 2023-08-13 13:06 | 0.24722
89 | 2023-08-20 12:20 | 5066 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 0 | 0 | 1 | Distance Relay Operated | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-20 13:15 | 0.038194
90 | 2023-08-31 08:55 | 5082 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 0 | 0 | 1 | Daudkandi Grid Control Panel work for SCADA. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-31 11:18 | 0.099306
91 | 2023-08-31 11:19 | 5084 | Cumilla | Cumilla | Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-2 | 0 | 0 | 1 | Daudkandi End SCADA operation test. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-31 13:10 | 0.077083
92 | 2023-08-04 16:10 | 2580 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 0 | 1 | 0 | PDB taken S/D for Work. | 0 | 1 | 0 | 0 | 1 | 0 | 20 | 2023-08-04 17:39 | 0.061806
93 | 2023-08-25 09:02 | 2620 | Cumilla | Cumilla | Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-1 | 0 | 0 | 1 | BUS SIDE ISOLATOR REALIGNMENT WORK SM NAGAR END . | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-25 18:09 | 0.37986
94 | 2023-08-20 10:12 | 8679 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Titas 50 MW Power Plant Line | 0 | 0 | 1 | 132 KV line touch by crane of Banglatrac | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-20 11:24 | 0.05
95 | 2023-08-22 05:55 | 8679 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Titas 50 MW Power Plant Line | 0 | 0 | 1 | Red Hot remove work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-22 08:41 | 0.11528
96 | 2023-08-29 09:02 | 8574 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 0 | 0 | 1 | 132 KV Sonargaon-1 Line Shutdown for SCADA Connection Work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-29 15:54 | 0.28611
97 | 2023-08-29 15:58 | 8676 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 0 | 0 | 1 | SCADA connection Work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-29 18:53 | 0.12153
98 | 2023-08-30 09:31 | 8387 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-1 HT | 0 | 1 | 0 | Scada Connection | 0 | 1 | 0 | 0 | 1 | 0 | 15 | 2023-08-30 13:56 | 0.18403
99 | 2023-08-30 14:00 | 8670 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-2 HT | 0 | 1 | 0 | Scada connection | 0 | 1 | 0 | 0 | 1 | 0 | 15 | 2023-08-30 16:01 | 0.084028
100 | 2023-08-30 16:13 | 8676 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 0 | 0 | 1 | Scada cnnection test | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-30 16:44 | 0.021528
101 | 2023-08-31 08:52 | 8677 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 0 | 0 | 1 | Cumilla(N)-1 Line shutdown for SCADA Connection work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-31 11:16 | 0.1
102 | 2023-08-31 11:19 | 8678 | Cumilla | Cumilla | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 0 | 0 | 1 | Cumilla(N)-2 shutdown for SCADA connection work. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-31 13:11 | 0.077778
103 | 2023-08-05 11:54 | 1828 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-2 | 0 | 0 | 1 | Line maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-05 12:48 | 0.0375
104 | 2023-08-10 07:12 | 1827 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-1 | 0 | 0 | 1 | Tripped (Tower No 54, Loop Jumper Out) | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-10 19:21 | 0.50625
105 | 2023-08-17 15:37 | 1823 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 0 | 0 | 1 | Un known | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-17 16:50 | 0.050694
106 | 2023-08-17 16:54 | 1823 | Cumilla | Cumilla | Cumilla | Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 0 | 0 | 1 | Tube well boring pipe touch the( B- Phase) live conductor of chauddagram ckt -2 between tower no. 482-483 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-17 19:35 | 0.11181
107 | 2023-08-19 14:58 | 9291 | Cumilla | Srimongol | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 0 | 0 | 1 | Emergency maintenance Ashugonj sub-station | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-19 16:38 | 0.069444
108 | 2023-08-01 12:00 | 1953 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 0 | 1 | 0 | Emergency loadshed Instructed by NLDC for Mainten Grid Voltage. | 0 | 0 | 1 | 0 | 1 | 0 | 32 | 2023-08-01 12:04 | 0.0027778
109 | 2023-08-04 15:59 | 1953 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 0 | 1 | 0 | due to PBS 33kv Chunarughat feeder trip showing E/F | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-04 16:02 | 0.0020833
110 | 2023-08-05 08:26 | 2369 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 0 | 1 | 0 | 33KV Feeder bus hot spot maintenance by PBS, Habigonj. Shutdown taken by PBS. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-05 08:59 | 0.022917
111 | 2023-08-16 11:24 | 2523 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 0 | 0 | 1 | None | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-16 11:33 | 0.00625
112 | 2023-08-24 08:07 | 1952 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 0 | 1 | 0 | 33 KV side Circuit Breaker loop joint hotspot Maintenance. Load flow by TR-04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-24 08:52 | 0.03125
113 | 2023-08-26 06:42 | 2521 | Cumilla | Srimongol | Sylhet | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 0 | 0 | 1 | S/D taken by Ashugonj Side.( Corrective maintenance at Ashugonj End) | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-26 07:16 | 0.023611
114 | 2023-08-16 11:24 | 3390 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | sreemangal-Shahjibazar circuit-2 | 0 | 0 | 1 | N/A | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-16 11:32 | 0.0055556
115 | 2023-08-31 13:39 | 3365 | Cumilla | Srimongol | Sylhet | Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 HT | 0 | 1 | 0 | Tr-2 132kV LA Change. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-31 17:06 | 0.14375
116 | 2023-08-06 12:02 | 3811 | Cumilla | Sylhet | Sylhet | Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 HT | 0 | 1 | 0 | 33 kv Red Hot | 0 | 0 | 1 | 0 | 1 | 0 | 20 | 2023-08-06 15:48 | 0.15694
117 | 2023-08-12 11:02 | 3811 | Cumilla | Sylhet | Sylhet | Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 HT | 0 | 1 | 0 | Development work | 0 | 1 | 0 | 0 | 1 | 0 | 10 | 2023-08-12 16:50 | 0.24167
118 | 2023-08-25 19:17 | 7803 | Cumilla | Sylhet | Sylhet | Chhatak 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | sunamganj 33kv pdb feeder trail. | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-25 19:22 | 0.0034722
119 | 2023-08-05 05:41 | 6772 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T1 HT | 0 | 1 | 0 | Red hot Maintenance CT to CB (33 KV R&Y Phase) | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-05 07:03 | 0.056944
120 | 2023-08-20 15:40 | 8799 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 0 | 0 | 1 | Schedule Maintenance Purpose. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-20 16:26 | 0.031944
121 | 2023-08-31 19:08 | 6786 | Cumilla | Sylhet | Sylhet | Sylhet 132/33kV Grid Sub-Station | T4 LT | 0 | 1 | 0 | Over load | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-31 21:38 | 0.10417
122 | 2023-08-03 17:17 | 26 | Dhaka (N) | Aricha | Dhaka | Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 0 | 1 | 0 | Pbs Feeder red hot | 0 | 0 | 1 | 0 | 1 | 0 | 30 | 2023-08-03 18:44 | 0.060417
123 | 2023-08-05 15:07 | 26 | Dhaka (N) | Aricha | Dhaka | Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 0 | 1 | 0 | Redhot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 30 | 2023-08-05 18:35 | 0.14444
124 | 2023-08-23 06:14 | 22 | Dhaka (N) | Aricha | Dhaka | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 0 | 1 | 0 | Red-hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-23 08:46 | 0.10556
125 | 2023-08-10 07:04 | 37 | Dhaka (N) | Dhaka (North) | Mymensingh | Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 0 | 1 | 0 | 33 bus cable change | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-10 10:57 | 0.16181
126 | 2023-08-18 06:06 | 138 | Dhaka (N) | Dhaka (North) | Mymensingh | Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 0 | 0 | 1 | Mymensingh side | 0 | 1 | 0 | 0 | 1 | 0 | 40 | 2023-08-18 10:43 | 0.19236
127 | 2023-08-05 13:28 | 876 | Dhaka (N) | Dhaka (North) | Dhaka | Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-1 | 0 | 0 | 1 | LA B-Phase Red hot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 57 | 2023-08-05 16:11 | 0.11319
128 | 2023-08-24 05:47 | 877 | Dhaka (N) | Dhaka (North) | Dhaka | Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 0 | 0 | 1 | R phase LA high temperature Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 80 | 2023-08-24 09:54 | 0.17153
129 | 2023-08-15 21:31 | 1465 | Dhaka (N) | Dhaka (North) | Dhaka | New Tongi 132/33kV Grid Sub-Station | New Tongi L-2 | 0 | 0 | 1 | Tr-2 Incomer 33kv to 33kv BUS cable fault | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-16 11:00 | 0.56181
130 | 2023-08-14 15:05 | 12335 | Dhaka (N) | Dhaka (North) | Dhaka | Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 0 | 0 | 1 | Distance Relay operate | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 15:40 | 0.024306
131 | 2023-08-04 04:25 | 1179 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 0 | 1 | 0 | DS-823 Maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-04 06:04 | 0.06875
132 | 2023-08-10 06:12 | 1203 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 0 | 0 | 1 | Shutdown taken by Kabirpur End via NLDC. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-10 07:50 | 0.068056
133 | 2023-08-19 10:45 | 1203 | Dhaka (N) | Dhaka (North) | Dhaka | Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 0 | 0 | 1 | For Kabirpur end Side Works | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-19 11:40 | 0.038194
134 | 2023-08-10 09:50 | 684 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 0 | 0 | 1 | Red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-10 15:16 | 0.22639
135 | 2023-08-14 14:15 | 11188 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-01 | 0 | 0 | 1 | Purpose of relay test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 16:36 | 0.097917
136 | 2023-08-21 10:36 | 11188 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-01 | 0 | 0 | 1 | Relay test | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-21 12:57 | 0.097917
137 | 2023-08-22 14:07 | 640 | Dhaka (N) | Dhaka(North-West) | Dhaka | Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 0 | 1 | 0 | Red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-22 16:47 | 0.11111
138 | 2023-08-05 09:41 | 12451 | Dhaka (N) | Dhaka(North-West) | Cumilla | Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 0 | 0 | 1 | Maintenance work at kishoreganj end | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-05 11:14 | 0.064583
139 | 2023-08-19 15:00 | 12453 | Dhaka (N) | Dhaka(North-West) | Cumilla | Ashuganj 230/132/33kV Sub-Station | B.Baria 132 kV Ckt-2 | 0 | 0 | 1 | R-phase CB oil filling | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-19 16:40 | 0.069444
140 | 2023-08-21 09:14 | 12448 | Dhaka (N) | Dhaka(North-West) | Cumilla | Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 0 | 0 | 1 | GIS project work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-21 16:38 | 0.30833
141 | 2023-08-22 09:04 | 12448 | Dhaka (N) | Dhaka(North-West) | Cumilla | Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 0 | 0 | 1 | 132kv GIS work purpose. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-22 18:37 | 0.39792
142 | 2023-08-22 20:52 | 11880 | Dhaka (N) | Dhaka(North-West) | Cumilla | Ashuganj 230/132/33kV Sub-Station | 230kV Busbar-1 | 1 | 0 | 0 | AIS (89-A) Bus isolator loop conductor cutting | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-22 21:11 | 0.013194
143 | 2023-08-13 10:05 | 1107 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) LT | 0 | 1 | 0 | For relay testing by System protection. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-13 16:07 | 0.25139
144 | 2023-08-13 16:09 | 1108 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 0 | 1 | 0 | Relay testing | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-13 18:04 | 0.079861
145 | 2023-08-16 16:19 | 1108 | Dhaka (N) | Dhaka(North-West) | Dhaka | Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 0 | 1 | 0 | 33 kV CB SF6 Gass Refill Work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-16 16:31 | 0.0083333
146 | 2023-08-28 10:40 | 990 | Dhaka (N) | Dhaka(North-West) | Dhaka | Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-2 HT | 0 | 1 | 0 | TC PRV TRV Trip, K-86-2OPTD, TRAFO TROVBLE RELAY-K355. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-28 12:10 | 0.0625
147 | 2023-08-16 10:18 | 126 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | Bus-B | 1 | 0 | 0 | DPBS-3 Shutdown for Red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-16 15:52 | 0.23194
148 | 2023-08-20 23:47 | 125 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | Bus-A | 1 | 0 | 0 | Red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-21 09:49 | 0.41806
149 | 2023-08-26 10:35 | 17 | Dhaka (N) | Dhaka(North-West) | Dhaka | Savar 132/33kV Grid Sub-Station | Transfer Bus | 1 | 0 | 0 | Alignment work of 132kV T-2 Main Bus-II DS (411M) | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-26 17:40 | 0.29514
150 | 2023-08-02 15:09 | 696 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | Main bus | 1 | 0 | 0 | Main bus shutdown due to 132 kV Kadda ckt-1 main bus DS (B phase) bus side connector red hot maintenance . | 0 | 0 | 1 | 0 | 1 | 0 | 20 | 2023-08-02 16:53 | 0.072222
151 | 2023-08-10 06:08 | 763 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 0 | 0 | 1 | red hot maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-10 07:49 | 0.070139
152 | 2023-08-20 15:14 | 756 | Dhaka (N) | Kaliakoir | Dhaka | Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 0 | 1 | 0 | 33KV Boroibari feeder Bus side red hot | 0 | 1 | 0 | 0 | 1 | 0 | 110 | 2023-08-20 16:51 | 0.067361
153 | 2023-08-14 10:20 | 537 | Dhaka (N) | Mymensingh | Mymensingh | Jamalpur 132/33kV Grid Sub-Station | 132KV PPM Jamalpur Power Plant | 0 | 0 | 1 | Disconncetor Switch Maintenance(Power plant end) | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 16:42 | 0.26528
154 | 2023-08-03 18:31 | 249 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 0 | 1 | 0 | Over Current- 33kv Itna Fauit O/C, E/F | 1 | 0 | 0 | 0 | 1 | 0 | 30 | 2023-08-03 18:39 | 0.0055556
155 | 2023-08-05 09:54 | 243 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 1 | 0 | 0 | Maintenance Work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-05 10:42 | 0.033333
156 | 2023-08-05 13:21 | 250 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 0 | 0 | 1 | Lightning | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-05 13:34 | 0.0090278
157 | 2023-08-22 12:24 | 248 | Dhaka (N) | Mymensingh | Mymensingh | Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 0 | 1 | 0 | 33KV Hossenpur Feeder Bus Connector Loop Burn Out. Shut Down Taken by PBS | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-22 14:35 | 0.090972
158 | 2023-08-12 06:20 | 16 | Dhaka (N) | Mymensingh | Mymensingh | Mymensingh 132/33kV Grid Sub-Station | Bus A | 1 | 0 | 0 | 132kV Solar Ckt Shut down due of High Temperature Maintenance in 132kV Solar Ckt A-Bus DS( 501S) -R & Y Phase Clamp. Shut down taken by Mr. Wang Hong Qiang, Manager, HDFC, Sinpower. | 0 | 1 | 0 | 0 | 1 | 0 | 185 | 2023-08-12 08:30 | 0.090278
159 | 2023-08-14 11:21 | 924 | Dhaka (N) | Mymensingh | Mymensingh | Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 0 | 1 | 0 | oiltc oil sample | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 12:04 | 0.029861
160 | 2023-08-14 12:11 | 913 | Dhaka (N) | Mymensingh | Mymensingh | Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 0 | 1 | 0 | oiltc oil sample | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 13:34 | 0.057639
161 | 2023-08-01 08:31 | 183 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 0 | 1 | 0 | Red hot at 33kv Jamuna feeder(PBS) at 33kv T3 bus section. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-01 10:23 | 0.077778
162 | 2023-08-02 00:10 | 185 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 0 | 1 | 0 | Red hot at 33kV bus side. | 0 | 0 | 1 | 0 | 1 | 0 | 14 | 2023-08-02 00:51 | 0.028472
163 | 2023-08-02 10:40 | 188 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | RPCL-1 | 0 | 0 | 1 | Distance Trip.(RPCL End) | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-02 10:55 | 0.010417
164 | 2023-08-14 16:04 | 185 | Dhaka (N) | Mymensingh | Mymensingh | Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 0 | 1 | 0 | Shakhipur 33kv feeder CT change | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 18:54 | 0.11806
165 | 2023-08-09 04:17 | 2728 | Dhaka (S) | Dhaka (Central) | Dhaka | Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 0 | 0 | 1 | Line fault | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-09 15:45 | 0.47778
166 | 2023-08-01 12:59 | 6128 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 0 | 0 | 1 | Trip due to Thunderstorm | 1 | 0 | 0 | 0 | 1 | 0 | 30 | 2023-08-01 13:11 | 0.0083333
167 | 2023-08-10 07:45 | 3287 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 0 | 0 | 1 | Shutdown given for Line resistance test(megger), due to circuit trip at 05:14 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-11 14:09 | 1.2667
168 | 2023-08-28 23:55 | 3285 | Dhaka (S) | Dhaka (Central) | Dhaka | Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 0 | 0 | 1 | Bhulta 230kV circuit-4 due to temperature rise(red hot) at Line DS 111S | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-29 09:29 | 0.39861
169 | 2023-08-01 12:48 | 8713 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 0 | 0 | 1 | Storm. | 1 | 0 | 0 | 0 | 1 | 0 | 55 | 2023-08-01 13:16 | 0.019444
170 | 2023-08-02 01:55 | 8713 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 0 | 0 | 1 | Unknown | 1 | 0 | 0 | 0 | 1 | 0 | 21 | 2023-08-02 02:10 | 0.010417
171 | 2023-08-09 06:21 | 8709 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Bhulta | 0 | 0 | 1 | CB to CT Loop Change Y phase | 0 | 1 | 0 | 0 | 1 | 0 | 70 | 2023-08-09 07:36 | 0.052083
172 | 2023-08-12 06:54 | 8710 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Narsingdi | 0 | 0 | 1 | Maintanance Work. | 0 | 1 | 0 | 0 | 1 | 0 | 57 | 2023-08-12 10:17 | 0.14097
173 | 2023-08-19 06:59 | 8714 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | EGCB 412MW | 0 | 0 | 1 | Jack bus to CB Loop Change Work . | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-19 15:49 | 0.36806
174 | 2023-08-28 11:27 | 8713 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 0 | 0 | 1 | Load Management by NLDC | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-28 16:40 | 0.21736
175 | 2023-08-30 11:12 | 8710 | Dhaka (S) | Dhaka (East) | Dhaka | Haripur 230/132kV Grid Sub-Station | Narsingdi | 0 | 0 | 1 | Trip | 1 | 0 | 0 | 0 | 1 | 0 | 80 | 2023-08-30 11:24 | 0.0083333
176 | 2023-08-08 09:55 | 2366 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 0 | 0 | 1 | Oli Filing | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-08 11:32 | 0.067361
177 | 2023-08-10 09:55 | 2363 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 0 | 0 | 1 | Oil leakage checking | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-10 11:57 | 0.084722
178 | 2023-08-11 09:45 | 2363 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 0 | 0 | 1 | Transformer Checking by EGCB. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-11 12:22 | 0.10903
179 | 2023-08-24 13:19 | 2364 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 0 | 0 | 1 | LBB INITIATION,86 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-24 13:44 | 0.017361
180 | 2023-08-30 15:41 | 2364 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 0 | 0 | 1 | A small pice telephone conductor hanging on Line conductor(B-phase)at EGCB plant end. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-30 16:02 | 0.014583
181 | 2023-08-08 09:57 | 2126 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 0 | 1 | 0 | OLTC Conservator Oil Level Low. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-08 11:30 | 0.064583
182 | 2023-08-13 00:58 | 2129 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 0 | 0 | 1 | emergency maintenance work | 0 | 0 | 1 | 0 | 1 | 0 | 225 | 2023-08-13 01:57 | 0.040972
183 | 2023-08-18 07:31 | 2129 | Dhaka (S) | Dhaka (East) | Dhaka | Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 0 | 0 | 1 | Transformer will work for Maniknagar end. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-18 18:31 | 0.45833
184 | 2023-08-06 07:14 | 5265 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 0 | 1 | 0 | S/D taken by PBS for corrective Maintenance . | 0 | 1 | 0 | 0 | 1 | 0 | 35 | 2023-08-06 09:23 | 0.089583
185 | 2023-08-09 13:17 | 5265 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 0 | 1 | 0 | Maintenance work of PBS at Bus section-01 under the Transformer of Tr-01. | 0 | 0 | 1 | 0 | 1 | 0 | 35 | 2023-08-09 15:03 | 0.073611
186 | 2023-08-24 21:10 | 5266 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 0 | 1 | 0 | PBS Sonargaon feeder trip | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-24 21:33 | 0.015972
187 | 2023-08-26 09:01 | 5265 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 0 | 1 | 0 | PBS 33kv kabilganj feeder Redhot maintenance. Work performed by PBS. | 0 | 1 | 0 | 0 | 1 | 0 | 30 | 2023-08-26 10:22 | 0.05625
188 | 2023-08-29 09:04 | 5267 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Duadkandi 1 | 0 | 0 | 1 | Shutdown taken by daudkandi Grid for maintenance purpose (Relay change). | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-29 15:54 | 0.28472
189 | 2023-08-29 16:00 | 8941 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 0 | 0 | 1 | Shutdown has been taken by Daudkandhi grid substation for maintenance purpose. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-29 18:52 | 0.11944
190 | 2023-08-30 16:15 | 8941 | Dhaka (S) | Dhaka (East) | Dhaka | Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 0 | 0 | 1 | SCADA integration of Daudkandi end. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-30 16:45 | 0.020833
191 | 2023-08-23 18:54 | 3354 | Dhaka (S) | Dhaka (South) | Dhaka | Hasnabad 132/33kV Grid Substation | Shitallakhya | 0 | 0 | 1 | Fire occurred at shitallakhya Sub-Station | 1 | 0 | 0 | 0 | 1 | 0 | -10 | 2023-08-23 19:34 | 0.027778
192 | 2023-08-18 06:52 | 6486 | Dhaka (S) | Dhaka (South) | Dhaka | Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 0 | 0 | 1 | LILO Connection out at APR Power Plant. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-18 21:03 | 0.59097
193 | 2023-08-19 07:13 | 6486 | Dhaka (S) | Dhaka (South) | Dhaka | Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 0 | 0 | 1 | LILO connection out at APR Power Plant. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-19 21:18 | 0.58681
194 | 2023-08-14 14:14 | 10768 | Dhaka (S) | Dhaka (South) | Dhaka | Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 0 | 0 | 1 | SPMD work at Aminbazar. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 16:38 | 0.1
195 | 2023-08-21 10:35 | 10768 | Dhaka (S) | Dhaka (South) | Dhaka | Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 0 | 0 | 1 | Maintenance work at aminbazar end. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-21 12:58 | 0.099306
196 | 2023-08-22 07:46 | 7755 | Dhaka (S) | Dhaka (South) | Dhaka | Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 HT | 0 | 1 | 0 | MOG related maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-22 10:54 | 0.13056
197 | 2023-08-01 17:09 | 12769 | Dhaka (S) | Dhaka (South) | Dhaka | Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 0 | 0 | 1 | General Trip | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-01 17:25 | 0.011111
198 | 2023-08-29 11:01 | 11468 | Dhaka (S) | Dhaka (South) | Dhaka | Shitalakhya 132/33kV Grid Sub-Station | 132 kV Bus-1 | 1 | 0 | 0 | Red hot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-29 12:42 | 0.070139
199 | 2023-08-18 06:55 | 6563 | Dhaka (S) | Dhaka (South) | Dhaka | Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 0 | 0 | 1 | Hasnabad grid will work at APR END | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-18 20:46 | 0.57708
200 | 2023-08-19 07:14 | 6563 | Dhaka (S) | Dhaka (South) | Dhaka | Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 0 | 0 | 1 | Hasnabad grid will work at APR Circuit | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-19 21:21 | 0.58819
201 | 2023-08-02 08:50 | 10434 | Dhaka (S) | Dhaka (South) | Dhaka | Srinagar 132/33kV Grid Sub-Station | Keraniganj-01 | 0 | 0 | 1 | Sreenagar- Keraniganj Line -01 Shutdown as per requist by NLDC for Keraniganj side work done. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-02 17:55 | 0.37847
202 | 2023-08-03 16:56 | 2752 | Dhaka (S) | Narsingdi | Dhaka | Bhulta 132/33kV Grid Sub-Station | GT1 LT | 0 | 1 | 0 | GT-1 33 kv side red hot maintenance work. | 0 | 1 | 0 | 0 | 1 | 0 | 70 | 2023-08-03 17:55 | 0.040972
203 | 2023-08-25 19:45 | 10105 | Dhaka (S) | Narsingdi | Dhaka | Bhulta 132/33kV Grid Sub-Station | GT2 HT | 0 | 1 | 0 | Huge red hot of LT bushing Y phase GT-2 | 0 | 0 | 1 | 0 | 1 | 0 | 50 | 2023-08-26 23:44 | 1.166
204 | 2023-08-29 06:49 | 2634 | Dhaka (S) | Narsingdi | Dhaka | Bhulta 132/33kV Grid Sub-Station | 132kV BUS | 1 | 0 | 0 | None | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-29 09:00 | 0.090972
205 | 2023-08-18 06:15 | 5276 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 0 | 1 | 0 | heating issues | 0 | 0 | 1 | 0 | 1 | 0 | 47 | 2023-08-18 08:43 | 0.10278
206 | 2023-08-31 21:10 | 5276 | Dhaka (S) | Narsingdi | Dhaka | Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 0 | 1 | 0 | 33KV (T3) CB Loop Connection Point Hotspot Mainteance Work. | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 2023-08-31 22:48 | 0.068056
207 | 2023-08-10 15:11 | 11138 | HVDC | HVDC | Khulna | BIPTC | Rajshahi-2 | 0 | 0 | 1 | Problem found in HVDC- Rajshahi Ckt-02 44 number tower | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-10 16:32 | 0.05625
208 | 2023-08-10 17:27 | 11130 | HVDC | HVDC | Khulna | BIPTC | Baharampur-3 | 0 | 0 | 1 | Tripped by distance relay | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-11 02:58 | 0.39653
209 | 2023-08-28 16:09 | 8160 | HVDC | Ishurdi | Rajshahi | Baghabari 230/132kV Grid Sub-Station | T-2 Bank HT | 0 | 1 | 0 | Maintenance work at PDB end. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-28 21:17 | 0.21389
210 | 2023-08-12 15:39 | 1908 | HVDC | Ishurdi | Rajshahi | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 1 | 0 | 0 | Bus isolator Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-12 18:11 | 0.10556
211 | 2023-08-25 07:26 | 2666 | HVDC | Ishurdi | Rajshahi | Pabna 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | New 33KV Square Feeder Bus Connection. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-25 09:47 | 0.097917
212 | 2023-08-28 15:27 | 4306 | HVDC | Ishurdi | Rajshahi | Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 0 | 0 | 1 | Only CB (113B) Open. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-29 00:55 | 0.39444
213 | 2023-08-01 09:54 | 10711 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 0 | 1 | 0 | 132 kV T-3 X-Former LT Busing (R-Phase) red-hot maintenance. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-01 10:45 | 0.035417
214 | 2023-08-01 16:58 | 10713 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 0 | 1 | 0 | 33 kV D/S R-Phase red hot | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-01 17:48 | 0.034722
215 | 2023-08-16 09:51 | 9759 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 0 | 1 | 0 | à¦•à¦¾à¦œ à¦•à¦°à¦¬à§‡ à§©à§© à¦•à§‡ à¦¬à¦¿ à¦à¦² à¦Ÿà¦¿ à¦¸à¦¾à¦‡à¦¡à§‡à¦° bushing à¦à¦° à¦°à§‡à¦¡ à¦¹à¦Ÿà¥¤ à§©à§© à¦•à§‡à¦¬à¦¿ à¦¬à¦¾à¦¸à§‡ à¦°à§‡à¦¡ à¦¹à¦Ÿ à¦ªà¦²à§à¦²à§€ à¦¬à¦¿à¦¦à§à¦¯à§à§Ž à¦•à¦°à§à¦¤à§ƒà¦ªà¦•à§à¦· à¦•à¦¾à¦œ à¦•à¦°à¦¬à§‡à¥¤ | 0 | 0 | 1 | 0 | 1 | 0 | 12 | 2023-08-16 11:15 | 0.058333
216 | 2023-08-19 11:29 | 10713 | HVDC | Ishurdi | Rajshahi | Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 0 | 1 | 0 | Red-hot maintanace 33 kv R phase DS for T-4 Transformer. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-19 13:37 | 0.088889
217 | 2023-08-28 14:20 | 1694 | HVDC | Jhenaidah | Khulna | Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 HT | 0 | 1 | 0 | PBS 33 kV feeder red hot repair | 0 | 1 | 0 | 0 | 1 | 0 | 22 | 2023-08-28 15:47 | 0.060417
218 | 2023-08-16 06:11 | 2635 | HVDC | Jhenaidah | Khulna | Kushtia 132/33kV Grid Sub-Station | T2 HT | 0 | 1 | 0 | 33 kv Isolator installation (koburhat feeder ,WZPDCL) | 0 | 1 | 0 | 0 | 1 | 0 | 35 | 2023-08-16 09:20 | 0.13125
219 | 2023-08-15 21:08 | 6812 | HVDC | Jhenaidah | Khulna | Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 0 | 0 | 1 | Thundering | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-15 21:18 | 0.0069444
220 | 2023-08-27 14:53 | 6812 | HVDC | Jhenaidah | Khulna | Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 0 | 0 | 1 | instructions by ALDC. Khulna. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-27 16:26 | 0.064583
221 | 2023-08-19 09:48 | 5728 | Khulna | Barisal | Barishal | Barguna 132/33kV Grid Sub-Station | Transformer-1 HT | 0 | 1 | 0 | 33 KV BREB-2 Feeder D/S load side Redhot Maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-19 11:50 | 0.084722
222 | 2023-08-01 11:19 | 7843 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 0 | 0 | 1 | Bad weather | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2023-08-01 11:26 | 0.0048611
223 | 2023-08-03 16:48 | 6743 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 0 | 1 | 0 | Self protection test | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-03 17:18 | 0.020833
224 | 2023-08-07 15:46 | 6726 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 0 | 1 | 0 | For dopdopia 2 feeder trial, | 1 | 0 | 0 | 0 | 1 | 0 | 45 | 2023-08-07 15:52 | 0.0041667
225 | 2023-08-10 09:45 | 6725 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 0 | 1 | 0 | To improve grounding system of T1 transformer | 0 | 0 | 1 | 0 | 1 | 0 | 17 | 2023-08-10 14:19 | 0.19028
226 | 2023-08-10 15:10 | 6743 | Khulna | Barisal | Barishal | Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 0 | 1 | 0 | To improve grounding system of T2 Transformer. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-10 23:24 | 0.34306
227 | 2023-08-26 06:31 | 5960 | Khulna | Barisal | Barishal | Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 0 | 1 | 0 | Red hot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 12 | 2023-08-26 08:03 | 0.063889
228 | 2023-08-30 16:17 | 5960 | Khulna | Barisal | Barishal | Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 0 | 1 | 0 | Same as LT | 0 | 1 | 0 | 0 | 1 | 0 | 10 | 2023-08-30 16:25 | 0.0055556
229 | 2023-08-06 09:26 | 3717 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 0 | 1 | 0 | Project Work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-06 12:22 | 0.12222
230 | 2023-08-06 12:43 | 3730 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 0 | 1 | 0 | Project work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-06 15:10 | 0.10208
231 | 2023-08-08 12:55 | 3796 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 0 | 0 | 1 | Project work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-08 17:21 | 0.18472
232 | 2023-08-09 08:53 | 3803 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 0 | 0 | 1 | Installation of Junction Box | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-09 13:45 | 0.20278
233 | 2023-08-15 14:08 | 3815 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 0 | 0 | 1 | Power Station End work | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-15 15:13 | 0.045139
234 | 2023-08-26 11:08 | 4578 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | 33 KV Bus | 1 | 0 | 0 | 33 kv harukandi feeder DS maintenance work | 0 | 0 | 1 | 0 | 1 | 0 | 22 | 2023-08-26 11:35 | 0.01875
235 | 2023-08-29 09:50 | 3763 | Khulna | Faridpur | Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 0 | 1 | 0 | Project Work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-29 12:02 | 0.091667
236 | 2023-08-11 07:16 | 3737 | Khulna | Faridpur | Khulna | Gopalganj 132/33kV Grid Sub-Station | T2 HT | 0 | 1 | 0 | 33 kv REB Feeder & bus joint maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 30 | 2023-08-11 10:53 | 0.15069
237 | 2023-08-27 07:27 | 3710 | Khulna | Faridpur | Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 HT | 0 | 1 | 0 | BPBS-1 red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 10 | 2023-08-27 08:46 | 0.054861
238 | 2023-08-04 09:38 | 12000 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 0 | 1 | 0 | Fire fighting work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-04 17:42 | 0.33611
239 | 2023-08-14 10:08 | 12000 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 0 | 1 | 0 | Fire fighting work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-14 18:09 | 0.33403
240 | 2023-08-27 10:24 | 11998 | Khulna | Faridpur | Khulna | Gopalganj 400/132kV Grid Sub-Station | ATR-02 HT | 0 | 1 | 0 | Fire protection work | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-30 16:48 | 3.2667
241 | 2023-08-08 12:48 | 9881 | Khulna | Faridpur | Khulna | Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 0 | 0 | 1 | Faridpur SS side work(Joint box replacement). | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-08 17:20 | 0.18889
242 | 2023-08-07 12:34 | 3685 | Khulna | Faridpur | Khulna | Shariatpur 132/33kV Grid Sub-Station | Main Bus - 1 | 1 | 0 | 0 | Bus coupler isolator ( Bus section -1) signal problem solution. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-07 19:07 | 0.27292
243 | 2023-08-14 23:26 | 3778 | Khulna | Khulna (N) | Khulna | Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) HT | 0 | 1 | 0 | T2 shutdown due to jikorgacha feeder redhot maintenance | 0 | 0 | 1 | 0 | 1 | 0 | 20 | 2023-08-15 01:13 | 0.074306
244 | 2023-08-24 06:12 | 4763 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- South -2 | 0 | 0 | 1 | CB & Bus Ds à¦à¦° à¦®à¦§à§à¦¯à§‡ Loop à¦à¦° String à¦•à§‡à¦Ÿà§‡ à¦¯à¦¾à¦“à§Ÿà¦¾ Loop à¦ªà¦°à¦¿à¦¬à¦°à§à¦¤à¦¨ à¦•à¦°à¦¾à¦° à¦œà¦¨à§à¦¯ à¦¸à¦¾à¦Ÿà¦¡à¦¾à¦‰à¦¨ à¦¦à§‡à¦“à§Ÿà¦¾ à¦¹à§Ÿà¥¤ | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-24 09:27 | 0.13542
245 | 2023-08-31 06:19 | 2693 | Khulna | Khulna (N) | Khulna | Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 0 | 1 | 0 | Red hot Maintenance 132 kv side R- phase CB. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-31 08:14 | 0.079861
246 | 2023-08-03 13:16 | 4923 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | TR1 (403-T) HT | 0 | 1 | 0 | Protection work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-03 13:34 | 0.0125
247 | 2023-08-03 13:55 | 4937 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | TR2 (413-T) HT | 0 | 1 | 0 | Protection work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-03 15:18 | 0.057639
248 | 2023-08-21 06:51 | 4937 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | TR2 (413-T) HT | 0 | 1 | 0 | Red hot maintenance work in 33 kV feeder No-06 | 0 | 1 | 0 | 0 | 1 | 0 | 25 | 2023-08-21 08:22 | 0.063194
249 | 2023-08-26 06:49 | 4937 | Khulna | Khulna (N) | Khulna | Narail 132/33kV Grid Sub-Station | TR2 (413-T) HT | 0 | 1 | 0 | Red hot maintenance in 33 kV feeder no-06 source side DS (y- phase) | 0 | 1 | 0 | 0 | 1 | 0 | 20 | 2023-08-26 08:48 | 0.082639
250 | 2023-08-03 13:12 | 3676 | Khulna | Khulna (N) | Khulna | Noapara 132/33kV Grid Sub-Station | T-4 HT | 0 | 1 | 0 | High Temp Maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 20 | 2023-08-03 14:04 | 0.036111
251 | 2023-08-09 09:01 | 2339 | Khulna | Khulna (N) | Khulna | Noapara 132/33kV Grid Sub-Station | BUS-B | 1 | 0 | 0 | Upgradation of B-Bus . | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-23 16:44 | 14.3215
252 | 2023-08-26 09:01 | 4362 | Khulna | Khulna (N) | Khulna | Noapara 132/33kV Grid Sub-Station | khulna central - 1 | 0 | 0 | 1 | Upgradation Work. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-26 12:40 | 0.15208
253 | 2023-08-01 12:56 | 4131 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 0 | 0 | 1 | Emergency tree trimming of span 12 to 13 Tower middle spot of 132 Kv Bagerhat- Bhandaria Line. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-01 13:41 | 0.03125
254 | 2023-08-16 13:04 | 4131 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 0 | 0 | 1 | Emergengy Tree trimming. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-16 13:45 | 0.028472
255 | 2023-08-26 07:22 | 5089 | Khulna | Khulna (S) | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) HT | 0 | 1 | 0 | 33 kv feeder rizar change work | 0 | 1 | 0 | 0 | 1 | 0 | 25 | 2023-08-26 10:15 | 0.12014
256 | 2023-08-09 17:03 | 7152 | Khulna | Khulna (S) | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 0 | 1 | 0 | Red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-09 17:59 | 0.038889
257 | 2023-08-22 14:44 | 11751 | Khulna | Khulna (S) | Khulna | Gollamari 132/33kV Grid Sub-Station | 132kV Bus Coupler | 1 | 0 | 0 | Remote Test, SPMD Khulna. | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2023-08-22 14:46 | 0.0013889
258 | 2023-08-01 12:28 | 6529 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 0 | 0 | 1 | Protection test work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-01 13:30 | 0.043056
259 | 2023-08-24 06:11 | 6532 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-2 | 0 | 0 | 1 | CB & DS Conductor Change for Central ss End. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-24 09:27 | 0.13611
260 | 2023-08-28 07:44 | 3725 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | TR-1 HT | 0 | 1 | 0 | Red hot maintenance work | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-28 11:22 | 0.15139
261 | 2023-08-28 11:33 | 3757 | Khulna | Khulna (S) | Khulna | Khulna(S) 230/132kV Grid Sub-Station | TR-2 HT | 0 | 1 | 0 | Over Heating Maintenance. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-28 14:41 | 0.13056
262 | 2023-08-10 08:34 | 1529 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 HT | 0 | 1 | 0 | 33 kv old port feeder loop disconnect | 1 | 0 | 0 | 0 | 1 | 0 | 12 | 2023-08-10 09:24 | 0.034722
263 | 2023-08-10 10:20 | 5366 | Khulna | Khulna (S) | Khulna | Mongla 132/33kV Grid Sub-Station | T-2 HT | 0 | 1 | 0 | 33 kv old port feeder loop reconnection | 0 | 0 | 1 | 0 | 1 | 0 | 12 | 2023-08-10 12:56 | 0.10833
264 | 2023-08-01 12:37 | 12458 | Khulna | Khulna (S) | Khulna | Rampal 400/230kV Grid Sub-Station | Khulna Line-2 | 0 | 0 | 1 | Remote command checking from NLDC | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-01 13:32 | 0.038194
265 | 2023-08-03 11:36 | 12461 | Khulna | Khulna (S) | Khulna | Rampal 400/230kV Grid Sub-Station | Generator Transformer-1 (GT-1) HT | 0 | 1 | 0 | Maintenance Work Purpose | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2023-08-14 15:16 | 11.1528
266 | 2023-08-04 09:05 | 2678 | Khulna | Khulna (S) | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 0 | 1 | 0 | Red hot maintenance | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2023-08-04 11:04 | 0.082639