## Western Zone Gen Load
|  | Peak Demand in Western Region (MW) |  |  | Line Capacity (MW)
Plant | Available Generation (MW) | Zone | Evening peak | Day Peak | Line | Transfer Capacity (MW)
Payra | 1240 | Khulna | 1850 | 1500 | EWIC-1 (Ghorashal - Ishurdi) | 200
Adani | 1500 | Rajshahi | 1700 | 1300 | EWIC-2 (Ashuganj - Sirajganj) | 500
Rampal | 1250 | Rangpur | 950 | 800 | EWIC-3 (Gopalganj - Aminbazar) | 850
Barapukuria | 300 | Barisal | 500 | 400 | Total | 2050
BEPCL | 300 | Total | 5000 | 4000
Sirajganj Unit-1, 2, 3, 4 | 700 | Surplus | 1830 | 2830
Bhola BPDB | 180
NBBL | 200
HVDC | 930
Northern HFO | 150
KPCL + Khan Jahan Ali | 80
Total | 6830

## Summary
Western Region
Derated Capacity (MW) | 8821
Time Period | 2023-05-01 | to | 2023-05-30
Scenario | Western Gen MW | Time | Western Load MW | Approx Gen Surplus MW
max gen in Western Zone | 5614 | 2023-05-22 22:00 | 4400.4 | 982
min gen in Western Zone | 2037 | 2023-05-18 06:00 | 1026 | 957
Avg gen in Western Zone (MW) | 4479.16

## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-05-30 | Wednesday
|  | Date (day): | 2019-05-30 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13057.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15031 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-05-29 | 2019-05-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 180 | 190 | 190
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 386 | 399 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 322 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 18 | 8 | 18 | 82 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 288 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 70 | 82 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 0 | 0 | 0 | 12 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 190 | 130 | 150 |  | 60 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 18 | 8 | 16 | 84 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 185 | 190 | 210 | 210 |  | 125 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 8 | 16 | 86 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 43 | 42 | 42 |  | 38 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 40 | 8 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 55 | 260 | 296 | 300 | 0
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 20 | 300 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 23 | 51 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 149 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 82 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 17 | 54 | 108 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 2707 | 3693 | 3390 | 3844 | 773 | 1222
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 9 | 20 | 18 | 40 | 10
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 222 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 62 | 50 | 64 |  | 34 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 47 | 51 | 51 | 68 |  | 34 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 55 | 45 | 80 | 20 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 90 | 50 | 90 | 10 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 5 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 16 | 92 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 69 | 300 | 87 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 90 | 38 | 90 | 10 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 18 | 163 | 18 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 1 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 805 | 1384 | 877 | 1472 | 668 | 398
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 203 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 305 | 310 | 320 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 305 | 310 | 320 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 40 | 43 | 43
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 167 | 175 | 175 | 175 | 20 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 132 | 13 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 39 | 40 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 120 | 34 | 120 | 80 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 11 | 16 | 16 |  | 6 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 136 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 16 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 19 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 98 | 100 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 34 | 97 | 27 | 105 | 8 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 22 | 97 | 18 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1396 | 1950 | 1592 | 2083 | 108 | 604
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 80 | 45 | 90 | 112 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 88 | 68 | 88 | 112 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 85 | 18 | 85 | 30 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 3 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 176 | 284 | 213.6 | 294 | 115 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 |  | 50 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST under maint.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 47 | 44 | 44
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 55 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 190 | 189 | 200 | 202 |  | 29 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 300 | 300 |  | 41 | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 369 | 368 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 380 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1633 | 1721 | 1770 | 1772 | 9 | 628
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 913 | 930 | 930
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 63 | 62 | 83 |  | 32 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 22 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 34 | 81 | 60 | 80 |  | 29 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 185 | 205 | 310 | 310 | 100 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 17 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 324 | 323 | 330 | 330 | 287 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 1669 | 1767 | 1944 | 1973 | 683 | 75
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 35 | 23 | 35 |  | 5 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 168 | 171 | 175 | 175
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 | 622 |  | Coal Shortage.
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 150 | 150 | 150 | 150
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 996 | 1144 | 1003 | 1148 | 716 | 225
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 25 | 30 |  | 22 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 35 |  | 36 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 21 | 28 | 28 | 28
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 141 | 194 | 210 | 210 | 0 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 164 | 176 | 210 | 210 | 10 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 346 | 377 | 0 | 200 | 214 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 35 | 35 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 14 | 20 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 46 | 88 | 80 | 90 |  | 14 | Fuel shortage
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 919 | 926 | 902 | 902 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1843 | 2069 | 1670 | 1957 | 980 | 116
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 74 | 71 | 74 | 11 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 12 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 32 | 48 | 35 | 49 |  | 6 | Engine problem
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 74 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 196 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 625 | 499 | 598 | 488 | 51 | 91
| Total |  |  |  |  | 24143 | 23370 | 11850 | 14511 | 13057.6 | 15031 | 4103 | 3359
A. |  | 2019-05-29 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14511 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11306 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15000 | MW
3 | Day peak Generation : |  |  | 11850 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14315.65 | MW
4 | Evening peak Generation : |  |  | 14511 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 467 | MW
5 | Total Energy Generation : |  | 296.7353 | MKWHr | By Solar | 3.3157 | MKWHr
| By Gas : | 155.5592 | MKWHr |  | By Oil: | 56.6391 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 55.9021 | MKWHr |  | By Hydro: | 0.30444 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.017424 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4103 | MW | Dhaka | 5157.85 | 5104.85 |  | 53 |  | 18:00 |  | 1128
|  |  | For Plants S/D or M/C prob = |  |  | 3359 | MW | Chittagong | 1472 | 1427 |  | 45 |  | 19:00 |  | 830.85
|  |  | Total = |  |  | 7462 | MW | Khulna | 1742.8 | 1669.8 |  | 73 |  | 19:30 |  | 685.69
7 | Total Gas Supplied : |  |  | 1212.08 | MMCFD |  |  | Rajshahi | 1443 | 1378 |  | 65 |  | 20:00 |  | 679.96
8 | Fuel Cost : | i) Gas : | Taka | 179049666.698 | ii) Oil : | Taka | 800812966.2 | Comilla | 1378 | 1283 |  | 95 |  | 21:00 |  | 466.995
|  | iii) Coal : | Taka | 182289704.29 | Total | Taka | 1162152337.188 | Mymensingh | 1150 | 1087 |  | 63 |  | 22:00 |  | 759.225
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 614 | 614 |  | 0 |  | 23:00 |  | 1355.145
| ii) During Peak Demand : |  |  | 700 | MW (E to W) at | 21:00 | hrs | Barisal | 448 | 405 |  | 43 |  | 24:00 |  | 1726.64
| iii) Maximum : |  |  | 660 | MW at | 22:00 | hrs | Rangpur | 910 | 880 |  | 30
10 | Maximum Temperature in Dhaka was |  |  |  | 37.2° C |  |  | Total | 14315.65 | 13848.65 |  | 467
B. |  | 2019-05-30 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 37.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 156 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15031 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13600 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 310.8247 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11312 | MW at | 7:00 | 40 | 22 | 21 | 20 | 15 | 14 | 10 | 0 | 14
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.385 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.87 |  | (b) Today: | 72.79 |  | (c) Rule Curve: |  | 76.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## pivot
Sum of gen_mw | Column Labels
Row Labels | Eastern | Western | Grand Total
2023-05-01 | 6598 | 3859 | 10457
2023-05-01 01:00 | 6558 | 4039 | 10597
2023-05-01 02:00 | 6447.2 | 3793 | 10240.2
2023-05-01 03:00 | 6184.2 | 3756 | 9940.2
2023-05-01 04:00 | 6079.2 | 3515 | 9594.2
2023-05-01 05:00 | 5949.2 | 3418 | 9367.2
2023-05-01 06:00 | 5605.2 | 3155.28 | 8760.48
2023-05-01 07:00 | 5532.2 | 3191.24 | 8723.44
2023-05-01 08:00 | 5130 | 3235.13 | 8365.13
2023-05-01 09:00 | 5113 | 3320.19 | 8433.19
2023-05-01 10:00 | 5307.5 | 3288.55 | 8596.05
2023-05-01 11:00 | 5821 | 3334.11 | 9155.11
2023-05-01 12:00 | 6075 | 3503.59 | 9578.59
2023-05-01 13:00 | 6343 | 3652.33 | 9995.33
2023-05-01 14:00 | 6541 | 3719.18 | 10260.18
2023-05-01 15:00 | 6490 | 3597.93 | 10087.93
2023-05-01 16:00 | 6440 | 3423.36 | 9863.36
2023-05-01 17:00 | 5949 | 3203.31 | 9152.31
2023-05-01 18:00 | 5979 | 3197 | 9176
2023-05-01 19:00 | 6928 | 3500 | 10428
2023-05-01 19:30 | 7053 | 3932.4 | 10985.4
2023-05-01 20:00 | 7031 | 3941 | 10972
2023-05-01 21:00 | 7150 | 4124 | 11274
2023-05-01 22:00 | 7155 | 4049 | 11204
2023-05-01 23:00 | 7035 | 4018 | 11053
2023-05-02 | 6849 | 3887 | 10736
2023-05-02 01:00 | 6638 | 3782 | 10420
2023-05-02 02:00 | 6416 | 3567 | 9983
2023-05-02 03:00 | 6206 | 3490 | 9696
2023-05-02 04:00 | 6093 | 3372 | 9465
2023-05-02 05:00 | 5985 | 3379 | 9364
2023-05-02 06:00 | 5826 | 3386.22 | 9212.22
2023-05-02 07:00 | 5950 | 3508.2 | 9458.2
2023-05-02 08:00 | 6122 | 3637.77 | 9759.77
2023-05-02 09:00 | 6346 | 3768.17 | 10114.17
2023-05-02 10:00 | 6670 | 4087.31 | 10757.31
2023-05-02 11:00 | 7199 | 4235.64 | 11434.64
2023-05-02 12:00 | 7646 | 4187.43 | 11833.43
2023-05-02 13:00 | 7722 | 4460.98 | 12182.98
2023-05-02 14:00 | 7515 | 4344.83 | 11859.83
2023-05-02 15:00 | 7662 | 4452.83 | 12114.83
2023-05-02 16:00 | 7670 | 4270.8 | 11940.8
2023-05-02 17:00 | 7683 | 4035.56 | 11718.56
2023-05-02 18:00 | 7387 | 3659.09 | 11046.09
2023-05-02 19:00 | 8513 | 4115 | 12628
2023-05-02 19:30 | 8746.79 | 4584 | 13330.79
2023-05-02 20:00 | 8707.79 | 4588 | 13295.79
2023-05-02 21:00 | 8551.79 | 4785 | 13336.79
2023-05-02 22:00 | 8453.99 | 4638 | 13091.99
2023-05-02 23:00 | 8159.99 | 4676.69 | 12836.68
2023-05-03 | 7656.99 | 4848 | 12504.99
2023-05-03 01:00 | 7187.2 | 4779 | 11966.2
2023-05-03 02:00 | 6935.2 | 4591 | 11526.2
2023-05-03 03:00 | 7017.2 | 4310 | 11327.2
2023-05-03 04:00 | 6890.2 | 4139.5 | 11029.7
2023-05-03 05:00 | 6887.2 | 4032.5 | 10919.7
2023-05-03 06:00 | 6639 | 3979.84 | 10618.84
2023-05-03 07:00 | 6659 | 4000.6 | 10659.6
2023-05-03 08:00 | 6539 | 4166.16 | 10705.16
2023-05-03 09:00 | 6796.5 | 4311.87 | 11108.37
2023-05-03 10:00 | 7495 | 4354.01 | 11849.01
2023-05-03 11:00 | 7710 | 4533.71 | 12243.71
2023-05-03 12:00 | 8024 | 4574 | 12598
2023-05-03 13:00 | 8165.5 | 4733.21 | 12898.71
2023-05-03 14:00 | 7806.5 | 4632.21 | 12438.71
2023-05-03 15:00 | 7042 | 4404.14 | 11446.14
2023-05-03 16:00 | 6933 | 4309.47 | 11242.47
2023-05-03 17:00 | 6873 | 4049.64 | 10922.64
2023-05-03 18:00 | 6645 | 4046.06 | 10691.06
2023-05-03 19:00 | 7551 | 4288 | 11839
2023-05-03 19:30 | 7789 | 4500 | 12289
2023-05-03 20:00 | 7920 | 4367 | 12287
2023-05-03 21:00 | 7857 | 4509 | 12366
2023-05-03 22:00 | 7610 | 4569 | 12179
2023-05-03 23:00 | 7479 | 4527 | 12006
2023-05-04 | 7039 | 4543 | 11582
2023-05-04 01:00 | 6765 | 4457 | 11222
2023-05-04 02:00 | 6550 | 4356 | 10906
2023-05-04 03:00 | 6502.2 | 4187 | 10689.2
2023-05-04 04:00 | 6394.2 | 3984 | 10378.2
2023-05-04 05:00 | 6214.2 | 3951 | 10165.2
2023-05-04 06:00 | 6023.2 | 3739.16 | 9762.36
2023-05-04 07:00 | 6043.2 | 3763.62 | 9806.82
2023-05-04 08:00 | 5954.2 | 3878.47 | 9832.67
2023-05-04 09:00 | 6092.2 | 4164.65 | 10256.85
2023-05-04 10:00 | 6198.2 | 4318.88 | 10517.08
2023-05-04 11:00 | 6523.2 | 4253.19 | 10776.39
2023-05-04 12:00 | 7010.2 | 4364.65 | 11374.85
2023-05-04 13:00 | 7089.2 | 4701.4 | 11790.6
2023-05-04 14:00 | 6839 | 4715.96 | 11554.96
2023-05-04 15:00 | 6911 | 4553.38 | 11464.38
2023-05-04 16:00 | 6897 | 4354.29 | 11251.29
2023-05-04 17:00 | 6442 | 4252.82 | 10694.82
2023-05-04 18:00 | 6343 | 4179.06 | 10522.06
2023-05-04 19:00 | 7622 | 4445 | 12067
2023-05-04 19:30 | 7839.2 | 4572 | 12411.2
2023-05-04 20:00 | 7871.2 | 4419 | 12290.2
2023-05-04 21:00 | 7696.2 | 4443 | 12139.2
2023-05-04 22:00 | 7426.2 | 4281 | 11707.2
2023-05-04 23:00 | 7290.2 | 4439 | 11729.2
2023-05-05 | 7124.2 | 4393 | 11517.2
2023-05-05 01:00 | 6607.2 | 4421 | 11028.2
2023-05-05 02:00 | 6450.2 | 4291 | 10741.2
2023-05-05 03:00 | 6241.2 | 4093 | 10334.2
2023-05-05 04:00 | 6114.2 | 4018 | 10132.2
2023-05-05 05:00 | 5990.2 | 3925 | 9915.2
2023-05-05 06:00 | 5532 | 3820.22 | 9352.22
2023-05-05 07:00 | 5658 | 3853.73 | 9511.73
2023-05-05 08:00 | 5679 | 4004.38 | 9683.38
2023-05-05 09:00 | 5719 | 3876.6 | 9595.6
2023-05-05 10:00 | 5861 | 4000.1 | 9861.1
2023-05-05 11:00 | 6048 | 4148.81 | 10196.81
2023-05-05 12:00 | 6223 | 4453.5 | 10676.5
2023-05-05 13:00 | 6492 | 4632.2 | 11124.2
2023-05-05 14:00 | 6298 | 4340.29 | 10638.29
2023-05-05 15:00 | 6641 | 4581.27 | 11222.27
2023-05-05 16:00 | 6464 | 4295.23 | 10759.23
2023-05-05 17:00 | 5969 | 4229.15 | 10198.15
2023-05-05 18:00 | 5878 | 4048.19 | 9926.19
2023-05-05 19:00 | 7418 | 4460 | 11878
2023-05-05 19:30 | 7891.2 | 4810 | 12701.2
2023-05-05 20:00 | 7948.2 | 4785 | 12733.2
2023-05-05 21:00 | 8263.2 | 4675 | 12938.2
2023-05-05 22:00 | 8217.2 | 4666 | 12883.2
2023-05-05 23:00 | 7962.2 | 4783 | 12745.2
2023-05-06 | 7461.2 | 4882 | 12343.2
2023-05-06 01:00 | 7016.2 | 4894 | 11910.2
2023-05-06 02:00 | 6922.2 | 4472 | 11394.2
2023-05-06 03:00 | 6845.2 | 4084 | 10929.2
2023-05-06 04:00 | 6679.2 | 4033 | 10712.2
2023-05-06 05:00 | 6359.2 | 4102 | 10461.2
2023-05-06 06:00 | 6026.2 | 4017.22 | 10043.42
2023-05-06 07:00 | 6039.2 | 4053.85 | 10093.05
2023-05-06 08:00 | 6175 | 4117.06 | 10292.06
2023-05-06 09:00 | 6417 | 4421.84 | 10838.84
2023-05-06 10:00 | 6700 | 4537.36 | 11237.36
2023-05-06 11:00 | 7167 | 4546.03 | 11713.03
2023-05-06 12:00 | 7237 | 4810.24 | 12047.24
2023-05-06 13:00 | 7284 | 5058.18 | 12342.18
2023-05-06 14:00 | 7226 | 5051.64 | 12277.64
2023-05-06 15:00 | 7291 | 5101.53 | 12392.53
2023-05-06 16:00 | 6875 | 4977 | 11852
2023-05-06 17:00 | 7080 | 4641.69 | 11721.69
2023-05-06 18:00 | 7207 | 4383.67 | 11590.67
2023-05-06 19:00 | 8182 | 4985.79 | 13167.79
2023-05-06 19:30 | 8892 | 5184.57 | 14076.57
2023-05-06 20:00 | 8863 | 5187.78 | 14050.78
2023-05-06 21:00 | 8794 | 5303 | 14097
2023-05-06 22:00 | 8484 | 5339 | 13823
2023-05-06 23:00 | 8125.2 | 5231 | 13356.2
2023-05-07 | 7471.2 | 5222 | 12693.2
2023-05-07 01:00 | 7044.2 | 5088 | 12132.2
2023-05-07 02:00 | 7035.2 | 5033 | 12068.2
2023-05-07 03:00 | 6932.2 | 4881 | 11813.2
2023-05-07 04:00 | 6852.2 | 4817 | 11669.2
2023-05-07 05:00 | 6771.2 | 4621 | 11392.2
2023-05-07 06:00 | 6448.2 | 4377.21 | 10825.41
2023-05-07 07:00 | 6480.2 | 4424.98 | 10905.18
2023-05-07 08:00 | 6532.2 | 4655.23 | 11187.43
2023-05-07 09:00 | 6896 | 4678.53 | 11574.53
2023-05-07 10:00 | 7594 | 4595.54 | 12189.54
2023-05-07 11:00 | 7978 | 4786.02 | 12764.02
2023-05-07 12:00 | 7984 | 4812.77 | 12796.77
2023-05-07 13:00 | 8148 | 4950.9 | 13098.9
2023-05-07 14:00 | 8076 | 4947.44 | 13023.44
2023-05-07 15:00 | 7714 | 4866.54 | 12580.54
2023-05-07 16:00 | 7470 | 4839 | 12309
2023-05-07 17:00 | 7487 | 4821.05 | 12308.05
2023-05-07 18:00 | 7410 | 4816.19 | 12226.19
2023-05-07 19:00 | 8700 | 5128 | 13828
2023-05-07 19:30 | 8797 | 5217 | 14014
2023-05-07 20:00 | 8853 | 5245 | 14098
2023-05-07 21:00 | 9000 | 5331.76 | 14331.76
2023-05-07 22:00 | 8943 | 5223.86 | 14166.86
2023-05-07 23:00 | 8517 | 5029 | 13546
2023-05-08 | 7981 | 5002.57 | 12983.57
2023-05-08 01:00 | 7600 | 5009.33 | 12609.33
2023-05-08 02:00 | 7448 | 5038.29 | 12486.29
2023-05-08 03:00 | 7281 | 4907.34 | 12188.34
2023-05-08 04:00 | 7220 | 4896.86 | 12116.86
2023-05-08 05:00 | 6937 | 4865.54 | 11802.54
2023-05-08 06:00 | 6609 | 4825.36 | 11434.36
2023-05-08 07:00 | 6545 | 4813.98 | 11358.98
2023-05-08 08:00 | 6506 | 4858.26 | 11364.26
2023-05-08 09:00 | 6768 | 4816.59 | 11584.59
2023-05-08 10:00 | 7036 | 4700.61 | 11736.61
2023-05-08 11:00 | 7229 | 4853 | 12082
2023-05-08 12:00 | 7478 | 4812.01 | 12290.01
2023-05-08 13:00 | 7435 | 4882.8 | 12317.8
2023-05-08 14:00 | 7239 | 4880.52 | 12119.52
2023-05-08 15:00 | 7290 | 4898.78 | 12188.78
2023-05-08 16:00 | 7559 | 4885.66 | 12444.66
2023-05-08 17:00 | 7669.2 | 4838.19 | 12507.39
2023-05-08 18:00 | 7529 | 4817.19 | 12346.19
2023-05-08 19:00 | 8680 | 5027 | 13707
2023-05-08 19:30 | 8649 | 5143 | 13792
2023-05-08 20:00 | 8763 | 5154 | 13917
2023-05-08 21:00 | 8852 | 5113 | 13965
2023-05-08 22:00 | 8709 | 5200 | 13909
2023-05-08 23:00 | 8512 | 5107 | 13619
2023-05-09 | 8153 | 5079 | 13232
2023-05-09 01:00 | 7701 | 5064 | 12765
2023-05-09 02:00 | 7452 | 5002 | 12454
2023-05-09 03:00 | 7340 | 4771 | 12111
2023-05-09 04:00 | 7265 | 4825 | 12090
2023-05-09 05:00 | 7157 | 4810 | 11967
2023-05-09 06:00 | 6939 | 4822.24 | 11761.24
2023-05-09 07:00 | 6867 | 4884.91 | 11751.91
2023-05-09 08:00 | 6879 | 4897.19 | 11776.19
2023-05-09 09:00 | 6900 | 4986.53 | 11886.53
2023-05-09 10:00 | 7530 | 5098.16 | 12628.16
2023-05-09 11:00 | 7993 | 4924.74 | 12917.74
2023-05-09 12:00 | 7937 | 5033.19 | 12970.19
2023-05-09 13:00 | 7762 | 5165.96 | 12927.96
2023-05-09 14:00 | 7365 | 5055.45 | 12420.45
2023-05-09 15:00 | 7586 | 4968.65 | 12554.65
2023-05-09 16:00 | 7413 | 4886.41 | 12299.41
2023-05-09 17:00 | 7394 | 4842.11 | 12236.11
2023-05-09 18:00 | 7462 | 5039.2 | 12501.2
2023-05-09 19:00 | 8552 | 5035 | 13587
2023-05-09 19:30 | 8537 | 5107 | 13644
2023-05-09 20:00 | 8575 | 5034 | 13609
2023-05-09 21:00 | 8757 | 4995 | 13752
2023-05-09 22:00 | 8851 | 5057 | 13908
2023-05-09 23:00 | 8113 | 4881 | 12994
2023-05-10 | 8023 | 4901 | 12924
2023-05-10 01:00 | 7953 | 4894 | 12847
2023-05-10 02:00 | 7532.5 | 4881 | 12413.5
2023-05-10 03:00 | 7439 | 4809 | 12248
2023-05-10 04:00 | 7293 | 4845 | 12138
2023-05-10 05:00 | 7301 | 4840 | 12141
2023-05-10 06:00 | 6826.8 | 4858.24 | 11685.04
2023-05-10 07:00 | 6627 | 4765.97 | 11392.97
2023-05-10 08:00 | 6676 | 4900.12 | 11576.12
2023-05-10 09:00 | 6750 | 4994.38 | 11744.38
2023-05-10 10:00 | 7370 | 5082.23 | 12452.23
2023-05-10 11:00 | 7932 | 5184.88 | 13116.88
2023-05-10 12:00 | 7934 | 5448.05 | 13382.05
2023-05-10 13:00 | 7914 | 5409.91 | 13323.91
2023-05-10 14:00 | 7538 | 5389.28 | 12927.28
2023-05-10 15:00 | 7601 | 5231.42 | 12832.42
2023-05-10 16:00 | 7331 | 5122 | 12453
2023-05-10 17:00 | 7223 | 4987.92 | 12210.92
2023-05-10 18:00 | 7106 | 4687.2 | 11793.2
2023-05-10 19:00 | 8568 | 4763 | 13331
2023-05-10 19:30 | 8771.5 | 5191 | 13962.5
2023-05-10 20:00 | 8524.5 | 5259 | 13783.5
2023-05-10 21:00 | 8696.5 | 5339 | 14035.5
2023-05-10 22:00 | 8721 | 5174 | 13895
2023-05-10 23:00 | 8434 | 5017 | 13451
2023-05-11 | 7673 | 5077 | 12750
2023-05-11 01:00 | 7350 | 4874 | 12224
2023-05-11 02:00 | 7190 | 4775 | 11965
2023-05-11 03:00 | 7107.7 | 4777 | 11884.7
2023-05-11 04:00 | 7062.2 | 4791 | 11853.2
2023-05-11 05:00 | 6954.2 | 4747 | 11701.2
2023-05-11 06:00 | 6684.2 | 4712.24 | 11396.44
2023-05-11 07:00 | 6546.2 | 4822.86 | 11369.06
2023-05-11 08:00 | 6591 | 4872.6 | 11463.6
2023-05-11 09:00 | 6642 | 4949.05 | 11591.05
2023-05-11 10:00 | 7257 | 5081.98 | 12338.98
2023-05-11 11:00 | 7644 | 5090.61 | 12734.61
2023-05-11 12:00 | 7685.5 | 5151.85 | 12837.35
2023-05-11 13:00 | 7737 | 5100.7 | 12837.7
2023-05-11 14:00 | 7441 | 4855.27 | 12296.27
2023-05-11 15:00 | 7370 | 4802.48 | 12172.48
2023-05-11 16:00 | 6998 | 4836.84 | 11834.84
2023-05-11 17:00 | 6913 | 4811.41 | 11724.41
2023-05-11 18:00 | 6985 | 4701.6 | 11686.6
2023-05-11 19:00 | 8072 | 4873 | 12945
2023-05-11 19:30 | 8084 | 4954 | 13038
2023-05-11 20:00 | 8213 | 4906 | 13119
2023-05-11 21:00 | 8525 | 4976 | 13501
2023-05-11 22:00 | 8406 | 5013 | 13419
2023-05-11 23:00 | 8203 | 4949 | 13152
2023-05-12 | 7525 | 4935 | 12460
2023-05-12 01:00 | 7105 | 4867 | 11972
2023-05-12 02:00 | 7007 | 4843 | 11850
2023-05-12 03:00 | 7085 | 4750 | 11835
2023-05-12 04:00 | 6965 | 4761 | 11726
2023-05-12 05:00 | 6761 | 4709 | 11470
2023-05-12 06:00 | 6383 | 4613.24 | 10996.24
2023-05-12 07:00 | 6214 | 4646.67 | 10860.67
2023-05-12 08:00 | 6204 | 4662.6 | 10866.6
2023-05-12 09:00 | 6055 | 4729.19 | 10784.19
2023-05-12 10:00 | 6187 | 4812.48 | 10999.48
2023-05-12 11:00 | 6392 | 4828.04 | 11220.04
2023-05-12 12:00 | 6842 | 4922.57 | 11764.57
2023-05-12 13:00 | 7026 | 5241.05 | 12267.05
2023-05-12 14:00 | 6888 | 4942.11 | 11830.11
2023-05-12 15:00 | 6930 | 4960.42 | 11890.42
2023-05-12 16:00 | 6806 | 4770.57 | 11576.57
2023-05-12 17:00 | 6853 | 4519.67 | 11372.67
2023-05-12 18:00 | 6884 | 4481.17 | 11365.17
2023-05-12 19:00 | 8162 | 4862.25 | 13024.25
2023-05-12 19:30 | 8517 | 5155 | 13672
2023-05-12 20:00 | 8680 | 5126 | 13806
2023-05-12 21:00 | 8581 | 5198 | 13779
2023-05-12 22:00 | 8550 | 5196.82 | 13746.82
2023-05-12 23:00 | 7930 | 4531 | 12461
2023-05-13 | 7088 | 4700 | 11788
2023-05-13 01:00 | 6509 | 4612 | 11121
2023-05-13 02:00 | 6474 | 4702 | 11176
2023-05-13 03:00 | 6297 | 4749 | 11046
2023-05-13 04:00 | 6177 | 4796 | 10973
2023-05-13 05:00 | 5940 | 4799 | 10739
2023-05-13 06:00 | 5668 | 4775 | 10443
2023-05-13 07:00 | 5385 | 4788.81 | 10173.81
2023-05-13 08:00 | 5225 | 4716.56 | 9941.56
2023-05-13 09:00 | 5169 | 4597.99 | 9766.99
2023-05-13 10:00 | 5296.5 | 4714.81 | 10011.31
2023-05-13 11:00 | 5662 | 4694.14 | 10356.14
2023-05-13 12:00 | 5888 | 4861.78 | 10749.78
2023-05-13 13:00 | 6083 | 4728 | 10811
2023-05-13 14:00 | 5867 | 4755 | 10622
2023-05-13 15:00 | 5751 | 4693.92 | 10444.92
2023-05-13 16:00 | 5969 | 4638.3 | 10607.3
2023-05-13 17:00 | 5855 | 4626.03 | 10481.03
2023-05-13 18:00 | 6056 | 4598.2 | 10654.2
2023-05-13 19:00 | 6942 | 4758 | 11700
2023-05-13 19:30 | 7029 | 5064 | 12093
2023-05-13 20:00 | 7077 | 5044 | 12121
2023-05-13 21:00 | 7243 | 5106 | 12349
2023-05-13 22:00 | 6907 | 5065 | 11972
2023-05-13 23:00 | 6381 | 4910 | 11291
2023-05-14 | 5936 | 4701 | 10637
2023-05-14 01:00 | 5681 | 4728 | 10409
2023-05-14 02:00 | 5393 | 4674 | 10067
2023-05-14 03:00 | 5372 | 4605 | 9977
2023-05-14 04:00 | 5273 | 4669 | 9942
2023-05-14 05:00 | 5307 | 4638 | 9945
2023-05-14 06:00 | 5226 | 4568.21 | 9794.21
2023-05-14 07:00 | 5202 | 4638.03 | 9840.03
2023-05-14 08:00 | 5124 | 4492.28 | 9616.28
2023-05-14 09:00 | 5193 | 4437.51 | 9630.51
2023-05-14 10:00 | 5203 | 4457.15 | 9660.15
2023-05-14 11:00 | 5204 | 4524.99 | 9728.99
2023-05-14 12:00 | 5252 | 4522.32 | 9774.32
2023-05-14 13:00 | 5320 | 4530 | 9850
2023-05-14 14:00 | 4694 | 4577 | 9271
2023-05-14 15:00 | 4875 | 4371.36 | 9246.36
2023-05-14 16:00 | 4564.5 | 4363.78 | 8928.28
2023-05-14 17:00 | 4548 | 4302.14 | 8850.14
2023-05-14 18:00 | 4687 | 4316.48 | 9003.48
2023-05-14 19:00 | 5446 | 4588 | 10034
2023-05-14 19:30 | 5709 | 4922 | 10631
2023-05-14 20:00 | 5699 | 5048 | 10747
2023-05-14 21:00 | 5972.79 | 5053 | 11025.79
2023-05-14 22:00 | 5879.79 | 5000 | 10879.79
2023-05-14 23:00 | 5467.79 | 4897 | 10364.79
2023-05-15 | 5067 | 4771 | 9838
2023-05-15 01:00 | 4860.79 | 4575 | 9435.79
2023-05-15 02:00 | 4732 | 4532 | 9264
2023-05-15 03:00 | 4850 | 4419 | 9269
2023-05-15 04:00 | 4823 | 4384 | 9207
2023-05-15 05:00 | 4822 | 4309 | 9131
2023-05-15 06:00 | 4763 | 4180.15 | 8943.15
2023-05-15 07:00 | 4841 | 4255.44 | 9096.44
2023-05-15 08:00 | 4814 | 4390.22 | 9204.22
2023-05-15 09:00 | 4825 | 4421.64 | 9246.64
2023-05-15 10:00 | 5099 | 4449.54 | 9548.54
2023-05-15 11:00 | 5375 | 4485.01 | 9860.01
2023-05-15 12:00 | 5505 | 4479.29 | 9984.29
2023-05-15 13:00 | 5562 | 4549.07 | 10111.07
2023-05-15 14:00 | 5440 | 4650.34 | 10090.34
2023-05-15 15:00 | 5442 | 4627.27 | 10069.27
2023-05-15 16:00 | 5493 | 4636.03 | 10129.03
2023-05-15 17:00 | 5518 | 4620.92 | 10138.92
2023-05-15 18:00 | 5638 | 4544.18 | 10182.18
2023-05-15 19:00 | 6418 | 4810 | 11228
2023-05-15 19:30 | 6587 | 4855 | 11442
2023-05-15 20:00 | 6819 | 4677 | 11496
2023-05-15 21:00 | 6974 | 4199 | 11173
2023-05-15 22:00 | 6815 | 4047 | 10862
2023-05-15 23:00 | 6151 | 4050 | 10201
2023-05-16 | 5275 | 4075 | 9350
2023-05-16 01:00 | 5051 | 4173 | 9224
2023-05-16 02:00 | 5184 | 4174 | 9358
2023-05-16 03:00 | 5182 | 4036 | 9218
2023-05-16 04:00 | 5117 | 4009 | 9126
2023-05-16 05:00 | 5107 | 3945 | 9052
2023-05-16 06:00 | 5003 | 3840.29 | 8843.29
2023-05-16 07:00 | 5017 | 3951.95 | 8968.95
2023-05-16 08:00 | 5105 | 4131.24 | 9236.24
2023-05-16 09:00 | 5046 | 4070.38 | 9116.38
2023-05-16 10:00 | 5506 | 4142.23 | 9648.23
2023-05-16 11:00 | 5632 | 4318.78 | 9950.78
2023-05-16 12:00 | 5781 | 4363 | 10144
2023-05-16 13:00 | 5552 | 4591.84 | 10143.84
2023-05-16 14:00 | 5538 | 4577.59 | 10115.59
2023-05-16 15:00 | 5527 | 4574.52 | 10101.52
2023-05-16 16:00 | 5516 | 4516.06 | 10032.06
2023-05-16 17:00 | 5513 | 4440.45 | 9953.45
2023-05-16 18:00 | 5337 | 4515.07 | 9852.07
2023-05-16 19:00 | 6281 | 4801 | 11082
2023-05-16 19:30 | 6537 | 4240 | 10777
2023-05-16 20:00 | 5460 | 3002 | 8462
2023-05-16 21:00 | 4634 | 3136 | 7770
2023-05-16 22:00 | 4754 | 3467 | 8221
2023-05-16 23:00 | 5160 | 3785 | 8945
2023-05-17 | 5468 | 4023 | 9491
2023-05-17 01:00 | 5657 | 4030 | 9687
2023-05-17 02:00 | 5433.5 | 4157 | 9590.5
2023-05-17 03:00 | 5281.5 | 4164 | 9445.5
2023-05-17 04:00 | 5059.5 | 3956 | 9015.5
2023-05-17 05:00 | 4878.5 | 3710 | 8588.5
2023-05-17 06:00 | 4784.5 | 3697.11 | 8481.61
2023-05-17 07:00 | 4621.5 | 3851.25 | 8472.75
2023-05-17 08:00 | 4619 | 3989 | 8608
2023-05-17 09:00 | 4653 | 3816.88 | 8469.88
2023-05-17 10:00 | 3988 | 3736.93 | 7724.93
2023-05-17 11:00 | 4676 | 3844.41 | 8520.41
2023-05-17 12:00 | 5397 | 3979.08 | 9376.08
2023-05-17 13:00 | 5578 | 4002.58 | 9580.58
2023-05-17 14:00 | 5612 | 4333.15 | 9945.15
2023-05-17 15:00 | 5911 | 4479.74 | 10390.74
2023-05-17 16:00 | 6128 | 4492.38 | 10620.38
2023-05-17 17:00 | 6089.7 | 4495.58 | 10585.28
2023-05-17 18:00 | 5939 | 4288.06 | 10227.06
2023-05-17 19:00 | 7146 | 4507 | 11653
2023-05-17 19:30 | 7279 | 4671 | 11950
2023-05-17 20:00 | 7248 | 4321 | 11569
2023-05-17 21:00 | 7332 | 4044 | 11376
2023-05-17 22:00 | 7010 | 4147 | 11157
2023-05-17 23:00 | 6756 | 4195 | 10951
2023-05-18 | 6265.5 | 4387 | 10652.5
2023-05-18 01:00 | 5856.5 | 4347 | 10203.5
2023-05-18 02:00 | 5697.5 | 3864 | 9561.5
2023-05-18 03:00 | 5208 | 3423 | 8631
2023-05-18 04:00 | 4886 | 2972 | 7858
2023-05-18 05:00 | 4308 | 2746 | 7054
2023-05-18 06:00 | 2922 | 2037 | 4959
2023-05-18 07:00 | 2910 | 2430 | 5340
2023-05-18 08:00 | 3470 | 2825.53 | 6295.53
2023-05-18 09:00 | 4046 | 2969.1 | 7015.1
2023-05-18 10:00 | 4658 | 3249.83 | 7907.83
2023-05-18 11:00 | 5440 | 3560.37 | 9000.37
2023-05-18 12:00 | 6101 | 3754.4 | 9855.4
2023-05-18 13:00 | 6091 | 4086.09 | 10177.09
2023-05-18 14:00 | 6031 | 4027.71 | 10058.71
2023-05-18 15:00 | 5991 | 4086.01 | 10077.01
2023-05-18 16:00 | 6001 | 4215.64 | 10216.64
2023-05-18 17:00 | 6125 | 4236.45 | 10361.45
2023-05-18 18:00 | 6116 | 4219 | 10335
2023-05-18 19:00 | 7018 | 4627.5 | 11645.5
2023-05-18 19:30 | 7119 | 4708 | 11827
2023-05-18 20:00 | 7193 | 4501 | 11694
2023-05-18 21:00 | 7241 | 4548 | 11789
2023-05-18 22:00 | 7054 | 4589 | 11643
2023-05-18 23:00 | 6641.5 | 4533 | 11174.5
2023-05-19 | 6300.5 | 4580 | 10880.5
2023-05-19 01:00 | 6051 | 4443 | 10494
2023-05-19 02:00 | 5776 | 4360 | 10136
2023-05-19 03:00 | 5603 | 4196 | 9799
2023-05-19 04:00 | 5376 | 4047 | 9423
2023-05-19 05:00 | 5251 | 3848 | 9099
2023-05-19 06:00 | 5065 | 3642.14 | 8707.14
2023-05-19 07:00 | 5136 | 3564.89 | 8700.89
2023-05-19 08:00 | 5136 | 3613.86 | 8749.86
2023-05-19 09:00 | 5327 | 3709.02 | 9036.02
2023-05-19 10:00 | 5425 | 3808.19 | 9233.19
2023-05-19 11:00 | 5773.5 | 4027.76 | 9801.26
2023-05-19 12:00 | 6007.5 | 4271.16 | 10278.66
2023-05-19 13:00 | 6097 | 4397.95 | 10494.95
2023-05-19 14:00 | 5885 | 4371 | 10256
2023-05-19 15:00 | 6165 | 4348.72 | 10513.72
2023-05-19 16:00 | 6145 | 4427.75 | 10572.75
2023-05-19 17:00 | 6073 | 4227.07 | 10300.07
2023-05-19 18:00 | 5780 | 4060.07 | 9840.07
2023-05-19 19:00 | 7201.5 | 4704 | 11905.5
2023-05-19 19:30 | 7387.5 | 5227 | 12614.5
2023-05-19 20:00 | 7412.5 | 5229 | 12641.5
2023-05-19 21:00 | 7464.5 | 5173 | 12637.5
2023-05-19 22:00 | 7411 | 4874 | 12285
2023-05-19 23:00 | 7097 | 4619 | 11716
2023-05-20 | 7072 | 4712 | 11784
2023-05-20 01:00 | 6450 | 4618 | 11068
2023-05-20 02:00 | 5873 | 4280 | 10153
2023-05-20 03:00 | 5546 | 3972 | 9518
2023-05-20 04:00 | 5174 | 3942 | 9116
2023-05-20 05:00 | 5098 | 3860 | 8958
2023-05-20 06:00 | 4855 | 3754 | 8609
2023-05-20 07:00 | 4927 | 3749.15 | 8676.15
2023-05-20 08:00 | 5052 | 3850.44 | 8902.44
2023-05-20 09:00 | 5286 | 4046.12 | 9332.12
2023-05-20 10:00 | 5673 | 4218.04 | 9891.04
2023-05-20 11:00 | 6218 | 4379.93 | 10597.93
2023-05-20 12:00 | 6281 | 4689 | 10970
2023-05-20 13:00 | 6149 | 4829.29 | 10978.29
2023-05-20 14:00 | 6434 | 4694.66 | 11128.66
2023-05-20 15:00 | 6216 | 4571.61 | 10787.61
2023-05-20 16:00 | 6055 | 4495.46 | 10550.46
2023-05-20 17:00 | 6089 | 4481.05 | 10570.05
2023-05-20 18:00 | 6466 | 4442.23 | 10908.23
2023-05-20 19:00 | 7771 | 4910 | 12681
2023-05-20 19:30 | 7763 | 5216 | 12979
2023-05-20 20:00 | 7811 | 5254 | 13065
2023-05-20 21:00 | 8109 | 5517 | 13626
2023-05-20 22:00 | 7908 | 5504 | 13412
2023-05-20 23:00 | 7416 | 5318 | 12734
2023-05-21 | 7010 | 5234 | 12244
2023-05-21 01:00 | 6674 | 5136 | 11810
2023-05-21 02:00 | 6497 | 5031 | 11528
2023-05-21 03:00 | 6425 | 5171 | 11596
2023-05-21 04:00 | 6217 | 5181 | 11398
2023-05-21 05:00 | 6233 | 4977 | 11210
2023-05-21 06:00 | 6156 | 4716.34 | 10872.34
2023-05-21 07:00 | 5963 | 4751.85 | 10714.85
2023-05-21 08:00 | 5942 | 4828.44 | 10770.44
2023-05-21 09:00 | 5934 | 4693.44 | 10627.44
2023-05-21 10:00 | 6313 | 4717.24 | 11030.24
2023-05-21 11:00 | 6665 | 4819.24 | 11484.24
2023-05-21 12:00 | 6782 | 5013.89 | 11795.89
2023-05-21 13:00 | 6900 | 4976.29 | 11876.29
2023-05-21 14:00 | 6702 | 5042.95 | 11744.95
2023-05-21 15:00 | 6490 | 4764.67 | 11254.67
2023-05-21 16:00 | 6228 | 4708 | 10936
2023-05-21 17:00 | 6224 | 4662.02 | 10886.02
2023-05-21 18:00 | 6593 | 4617.03 | 11210.03
2023-05-21 19:00 | 7615 | 4796 | 12411
2023-05-21 19:30 | 7597 | 4936 | 12533
2023-05-21 20:00 | 7511 | 4867 | 12378
2023-05-21 21:00 | 6213 | 4159 | 10372
2023-05-21 22:00 | 5254 | 3660 | 8914
2023-05-21 23:00 | 5273 | 3760 | 9033
2023-05-22 | 5445 | 3731 | 9176
2023-05-22 01:00 | 5326 | 3846 | 9172
2023-05-22 02:00 | 5345.5 | 3847 | 9192.5
2023-05-22 03:00 | 5269 | 3910 | 9179
2023-05-22 04:00 | 5264 | 3914 | 9178
2023-05-22 05:00 | 5271 | 3816 | 9087
2023-05-22 06:00 | 5125 | 3738.34 | 8863.34
2023-05-22 07:00 | 5219 | 3788.1 | 9007.1
2023-05-22 08:00 | 5266 | 4001.38 | 9267.38
2023-05-22 09:00 | 5804.5 | 4244.63 | 10049.13
2023-05-22 10:00 | 6299 | 4306.43 | 10605.43
2023-05-22 11:00 | 6571 | 4514.68 | 11085.68
2023-05-22 12:00 | 6956.79 | 4794.09 | 11750.88
2023-05-22 13:00 | 7105.79 | 5029.78 | 12135.57
2023-05-22 14:00 | 7094.79 | 4934.39 | 12029.18
2023-05-22 15:00 | 7098.79 | 4949.34 | 12048.13
2023-05-22 16:00 | 7199.79 | 4953.2 | 12152.99
2023-05-22 17:00 | 7129.79 | 4923.88 | 12053.67
2023-05-22 18:00 | 7190.79 | 4859.17 | 12049.96
2023-05-22 19:00 | 8285.79 | 5107 | 13392.79
2023-05-22 19:30 | 8154.79 | 5399 | 13553.79
2023-05-22 20:00 | 8278.79 | 5382 | 13660.79
2023-05-22 21:00 | 8405.79 | 5532 | 13937.79
2023-05-22 22:00 | 8179.79 | 5614 | 13793.79
2023-05-22 23:00 | 7896.79 | 5509 | 13405.79
2023-05-23 | 7605.79 | 5447 | 13052.79
2023-05-23 01:00 | 7197.79 | 5412 | 12609.79
2023-05-23 02:00 | 7094.79 | 5419 | 12513.79
2023-05-23 03:00 | 6879.79 | 5369 | 12248.79
2023-05-23 04:00 | 6721.79 | 5278 | 11999.79
2023-05-23 05:00 | 6662.79 | 5231 | 11893.79
2023-05-23 06:00 | 6517.79 | 4867.09 | 11384.88
2023-05-23 07:00 | 6375.79 | 4924.32 | 11300.11
2023-05-23 08:00 | 6361.79 | 4953.79 | 11315.58
2023-05-23 09:00 | 6457.79 | 4962.13 | 11419.92
2023-05-23 10:00 | 6761.79 | 5008.5 | 11770.29
2023-05-23 11:00 | 6716.79 | 5115 | 11831.79
2023-05-23 12:00 | 6920.79 | 5301.89 | 12222.68
2023-05-23 13:00 | 6812.79 | 5294.64 | 12107.43
2023-05-23 14:00 | 6048.79 | 4657.35 | 10706.14
2023-05-23 15:00 | 6000 | 4330.53 | 10330.53
2023-05-23 16:00 | 5726 | 3721 | 9447
2023-05-23 17:00 | 5464 | 3243 | 8707
2023-05-23 18:00 | 3772 | 2695 | 6467
2023-05-23 19:00 | 3892 | 2755 | 6647
2023-05-23 19:30 | 4131 | 2935 | 7066
2023-05-23 20:00 | 4341 | 3267 | 7608
2023-05-23 21:00 | 5075 | 3271 | 8346
2023-05-23 22:00 | 5460 | 3339 | 8799
2023-05-23 23:00 | 5399 | 3361 | 8760
2023-05-24 | 5604 | 3402 | 9006
2023-05-24 01:00 | 5501 | 3454 | 8955
2023-05-24 02:00 | 5316 | 3436 | 8752
2023-05-24 03:00 | 5221 | 3412 | 8633
2023-05-24 04:00 | 4891 | 3363 | 8254
2023-05-24 05:00 | 4818 | 3353 | 8171
2023-05-24 06:00 | 4592.79 | 3509.18 | 8101.97
2023-05-24 07:00 | 4869.79 | 3673.09 | 8542.88
2023-05-24 08:00 | 5069.79 | 3815.3 | 8885.09
2023-05-24 09:00 | 5406.79 | 3961.35 | 9368.14
2023-05-24 10:00 | 5271.79 | 3919.87 | 9191.66
2023-05-24 11:00 | 5642.79 | 4229.23 | 9872.02
2023-05-24 12:00 | 5944.79 | 4090.37 | 10035.16
2023-05-24 13:00 | 6028.79 | 4514.33 | 10543.12
2023-05-24 14:00 | 6111.79 | 4621.86 | 10733.65
2023-05-24 15:00 | 6274.79 | 4615.81 | 10890.6
2023-05-24 16:00 | 6502.79 | 4592.61 | 11095.4
2023-05-24 17:00 | 6426.79 | 4314.16 | 10740.95
2023-05-24 18:00 | 6277.79 | 4258.25 | 10536.04
2023-05-24 19:00 | 7239.79 | 4745 | 11984.79
2023-05-24 19:30 | 7381.79 | 5265 | 12646.79
2023-05-24 20:00 | 7361.79 | 5042 | 12403.79
2023-05-24 21:00 | 7283.79 | 4986 | 12269.79
2023-05-24 22:00 | 7024.79 | 4940 | 11964.79
2023-05-24 23:00 | 6647.79 | 4938 | 11585.79
2023-05-25 | 6567.79 | 4751 | 11318.79
2023-05-25 01:00 | 6134.79 | 4753 | 10887.79
2023-05-25 02:00 | 5908.79 | 4600 | 10508.79
2023-05-25 03:00 | 5654.79 | 4473 | 10127.79
2023-05-25 04:00 | 5406.79 | 4379 | 9785.79
2023-05-25 05:00 | 5056.79 | 4336 | 9392.79
2023-05-25 06:00 | 4678 | 4247.14 | 8925.14
2023-05-25 07:00 | 4754 | 4342.08 | 9096.08
2023-05-25 08:00 | 4806 | 4440.46 | 9246.46
2023-05-25 09:00 | 5615.79 | 4451.54 | 10067.33
2023-05-25 10:00 | 5991 | 4692.35 | 10683.35
2023-05-25 11:00 | 6453.79 | 4814.21 | 11268
2023-05-25 12:00 | 6746.79 | 5001.27 | 11748.06
2023-05-25 13:00 | 6933.79 | 4993.29 | 11927.08
2023-05-25 14:00 | 6999.79 | 5117.58 | 12117.37
2023-05-25 15:00 | 7090.79 | 4977.11 | 12067.9
2023-05-25 16:00 | 6787.79 | 4772.11 | 11559.9
2023-05-25 17:00 | 6848.79 | 4728 | 11576.79
2023-05-25 18:00 | 6759 | 4445.23 | 11204.23
2023-05-25 19:00 | 8172.79 | 4831 | 13003.79
2023-05-25 19:30 | 8369.79 | 5121 | 13490.79
2023-05-25 20:00 | 8305.79 | 5202 | 13507.79
2023-05-25 21:00 | 8028.79 | 3905 | 11933.79
2023-05-25 22:00 | 7168.79 | 3877 | 11045.79
2023-05-25 23:00 | 6271.79 | 3311 | 9582.79
2023-05-26 | 5847 | 3232 | 9079
2023-05-26 01:00 | 5761 | 3298 | 9059
2023-05-26 02:00 | 5699 | 3350 | 9049
2023-05-26 03:00 | 5582 | 3393 | 8975
2023-05-26 04:00 | 5590 | 3381 | 8971
2023-05-26 05:00 | 5283 | 3348 | 8631
2023-05-26 06:00 | 4801 | 3268.27 | 8069.27
2023-05-26 07:00 | 4797 | 3238.92 | 8035.92
2023-05-26 08:00 | 4728 | 3427.56 | 8155.56
2023-05-26 09:00 | 5184 | 3398.93 | 8582.93
2023-05-26 10:00 | 5499.79 | 3516.8 | 9016.59
2023-05-26 11:00 | 5978.79 | 3608.08 | 9586.87
2023-05-26 12:00 | 6462.99 | 3822.8 | 10285.79
2023-05-26 13:00 | 6647.79 | 4305 | 10952.79
2023-05-26 14:00 | 6608 | 4069.58 | 10677.58
2023-05-26 15:00 | 6930.79 | 4280.08 | 11210.87
2023-05-26 16:00 | 6882 | 4098.35 | 10980.35
2023-05-26 17:00 | 6670 | 3859.9 | 10529.9
2023-05-26 18:00 | 6538 | 3721.06 | 10259.06
2023-05-26 19:00 | 7951.79 | 4306 | 12257.79
2023-05-26 19:30 | 7781 | 4767 | 12548
2023-05-26 20:00 | 7637 | 4671 | 12308
2023-05-26 21:00 | 7704 | 4208 | 11912
2023-05-26 22:00 | 7210 | 4103 | 11313
2023-05-26 23:00 | 6942.79 | 4300 | 11242.79
2023-05-27 | 6940.79 | 4563 | 11503.79
2023-05-27 01:00 | 6813.79 | 4485 | 11298.79
2023-05-27 02:00 | 6486.79 | 4492 | 10978.79
2023-05-27 03:00 | 6444.79 | 4184 | 10628.79
2023-05-27 04:00 | 6295.79 | 3991 | 10286.79
2023-05-27 05:00 | 6062.79 | 3819 | 9881.79
2023-05-27 06:00 | 5873 | 3668.31 | 9541.31
2023-05-27 07:00 | 5855 | 3710.79 | 9565.79
2023-05-27 08:00 | 5977 | 3809.76 | 9786.76
2023-05-27 09:00 | 6192.79 | 3949.23 | 10142.02
2023-05-27 10:00 | 6306.79 | 4028.29 | 10335.08
2023-05-27 11:00 | 6448.27 | 4109.43 | 10557.7
2023-05-27 12:00 | 6567.79 | 4213.83 | 10781.62
2023-05-27 13:00 | 6425 | 4151.73 | 10576.73
2023-05-27 14:00 | 6210 | 4119.87 | 10329.87
2023-05-27 15:00 | 6301.79 | 4186.74 | 10488.53
2023-05-27 16:00 | 6162.79 | 4053 | 10215.79
2023-05-27 17:00 | 6240.79 | 3994.31 | 10235.1
2023-05-27 18:00 | 6222 | 3914.25 | 10136.25
2023-05-27 19:00 | 7749.79 | 4156 | 11905.79
2023-05-27 19:30 | 8217.79 | 4578 | 12795.79
2023-05-27 20:00 | 8087.79 | 4734 | 12821.79
2023-05-27 21:00 | 8162.79 | 4622 | 12784.79
2023-05-27 22:00 | 7844.79 | 4539 | 12383.79
2023-05-27 23:00 | 7586.79 | 4538 | 12124.79
2023-05-28 | 7212.79 | 4596 | 11808.79
2023-05-28 01:00 | 6974.79 | 4458 | 11432.79
2023-05-28 02:00 | 6786.79 | 4070.5 | 10857.29
2023-05-28 03:00 | 6554.79 | 3872.9 | 10427.69
2023-05-28 04:00 | 6439.79 | 3718.9 | 10158.69
2023-05-28 05:00 | 6234.79 | 3674.9 | 9909.69
2023-05-28 06:00 | 5991.79 | 3659.18 | 9650.97
2023-05-28 07:00 | 6198.79 | 3706.9 | 9905.69
2023-05-28 08:00 | 6316.79 | 3892.43 | 10209.22
2023-05-28 09:00 | 6627.79 | 4046.91 | 10674.7
2023-05-28 10:00 | 7020.79 | 4219.5 | 11240.29
2023-05-28 11:00 | 7113.79 | 4402.19 | 11515.98
2023-05-28 12:00 | 7201.79 | 4597.2 | 11798.99
2023-05-28 13:00 | 7212.79 | 4822.1 | 12034.89
2023-05-28 14:00 | 7183.79 | 4842.54 | 12026.33
2023-05-28 15:00 | 7416.29 | 4798.77 | 12215.06
2023-05-28 16:00 | 7345.29 | 4702.53 | 12047.82
2023-05-28 17:00 | 7104.79 | 4733.15 | 11837.94
2023-05-28 18:00 | 6845 | 4738.28 | 11583.28
2023-05-28 19:00 | 8314.79 | 5032 | 13346.79
2023-05-28 19:30 | 8811.79 | 5280 | 14091.79
2023-05-28 20:00 | 8573.79 | 5360 | 13933.79
2023-05-28 21:00 | 8870.79 | 5266 | 14136.79
2023-05-28 22:00 | 8791.79 | 5134 | 13925.79
2023-05-28 23:00 | 8441.79 | 5044 | 13485.79
2023-05-29 | 7862.79 | 5023 | 12885.79
2023-05-29 01:00 | 7505.79 | 4770 | 12275.79
2023-05-29 02:00 | 7326.79 | 4768 | 12094.79
2023-05-29 03:00 | 7129.79 | 4648 | 11777.79
2023-05-29 04:00 | 7069.79 | 4625 | 11694.79
2023-05-29 05:00 | 6868.79 | 4593 | 11461.79
2023-05-29 06:00 | 6571 | 4389.28 | 10960.28
2023-05-29 07:00 | 6591 | 4456.04 | 11047.04
2023-05-29 08:00 | 6691.79 | 4527.34 | 11219.13
2023-05-29 09:00 | 6706.79 | 4544.61 | 11251.4
2023-05-29 10:00 | 6709 | 4552.73 | 11261.73
2023-05-29 11:00 | 6761 | 4649.39 | 11410.39
2023-05-29 12:00 | 7343.79 | 4591.29 | 11935.08
2023-05-29 13:00 | 7271.79 | 4655.26 | 11927.05
2023-05-29 14:00 | 7209.79 | 4640.29 | 11850.08
2023-05-29 15:00 | 7054.79 | 4663.76 | 11718.55
2023-05-29 16:00 | 6983.79 | 4591.2 | 11574.99
2023-05-29 17:00 | 7140.79 | 4504.16 | 11644.95
2023-05-29 18:00 | 6935 | 4515.23 | 11450.23
2023-05-29 19:00 | 8391 | 4868 | 13259
2023-05-29 19:30 | 8664.79 | 5048 | 13712.79
2023-05-29 20:00 | 8914.79 | 5131 | 14045.79
2023-05-29 21:00 | 9196.79 | 5140 | 14336.79
2023-05-29 22:00 | 8663.79 | 5048 | 13711.79
2023-05-29 23:00 | 8000.79 | 5013 | 13013.79
2023-05-30 | 7579.79 | 4964 | 12543.79
2023-05-30 01:00 | 7422.79 | 4834 | 12256.79
2023-05-30 02:00 | 7331.79 | 4802 | 12133.79
2023-05-30 03:00 | 7161.79 | 4813 | 11974.79
2023-05-30 04:00 | 7137.79 | 4822 | 11959.79
2023-05-30 05:00 | 6995.79 | 4763 | 11758.79
2023-05-30 06:00 | 6646.79 | 4743.3 | 11390.09
2023-05-30 07:00 | 6436 | 4870.02 | 11306.02
2023-05-30 08:00 | 6585 | 4866.23 | 11451.23
2023-05-30 09:00 | 6489 | 4951.37 | 11440.37
2023-05-30 10:00 | 6276 | 4947.95 | 11223.95
2023-05-30 11:00 | 6384 | 4968.01 | 11352.01
2023-05-30 12:00 | 6717.79 | 5133.41 | 11851.2
2023-05-30 13:00 | 7080.8 | 5093.38 | 12174.18
2023-05-30 14:00 | 7193.1 | 5090.71 | 12283.81
2023-05-30 15:00 | 7256.69 | 5053.83 | 12310.52
2023-05-30 16:00 | 7132.56 | 4945.54 | 12078.1
2023-05-30 17:00 | 6825.79 | 4911.1 | 11736.89
2023-05-30 18:00 | 6925.79 | 4894.23 | 11820.02
2023-05-30 19:00 | 8417 | 5213 | 13630
2023-05-30 19:30 | 8793 | 5239 | 14032
2023-05-30 20:00 | 8838 | 5350 | 14188
2023-05-30 21:00 | 9032.79 | 5479 | 14511.79
2023-05-30 22:00 | 8838.79 | 5267 | 14105.79
2023-05-30 23:00 | 8292.79 | 5139 | 13431.79
Grand Total | 4976567.44 | 3359369.14 | 8335936.58

## Max Gen W
Maximum Load: 13306.60 MW at 21:00 hrs.
Download
Hour | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total Load (MW) | W Load
0:00 | 3583.91 | 1188.2 | 827 | 488 | 351 | 1034.6 | 400 | 543.2 | 584 | 8999.91 | 2561.8
1:00 | 3322.2 | 1239 | 836 | 487 | 339 | 953 | 380.2 | 651.8 | 576 | 8784.2 | 2561
2:00 | 3335.7 | 1223.5 | 859 | 519 | 332 | 1076.8 | 290.9 | 674.8 | 536 | 8847.7 | 2578.5
3:00 | 3345.2 | 1092.8 | 812 | 492 | 323 | 1077.6 | 312.8 | 684.8 | 530 | 8670.2 | 2605.2
4:00 | 3344.9 | 1130.3 | 816 | 491 | 309 | 1088.4 | 298.2 | 689.8 | 504 | 8671.6 | 2580.4
5:00 | 3341.9 | 1087.4 | 813 | 497 | 283 | 1055.6 | 301.2 | 668.8 | 480 | 8527.9 | 2505.6
6:00 | 3330.9 | 1085.9 | 793 | 506 | 269 | 1064.8 | 264.8 | 688.8 | 492 | 8495.2 | 2510.4
7:00 | 3432 | 1073.3 | 786 | 447 | 279 | 1072.8 | 265 | 737.8 | 554 | 8646.9 | 2629.6
8:00 | 3725.6 | 1107 | 805 | 482 | 283 | 1054.2 | 255 | 746 | 571 | 9028.8 | 2626.2
9:00 | 4164.3 | 1126.24 | 808 | 587 | 294 | 1066.6 | 253.3 | 819.2 | 554 | 9672.64 | 2693.1
10:00 | 4433 | 1094.2 | 781 | 605 | 343 | 1138.5 | 276 | 892.2 | 491 | 10053.9 | 2797.7
11:00 | 4705 | 1036.3 | 824 | 681 | 339 | 1197.2 | 323 | 965 | 584 | 10654.5 | 3069.2
12:00 | 4946.1 | 1032.6 | 820 | 704 | 385 | 1308.4 | 337 | 1039 | 611 | 11183.1 | 3295.4
13:00 | 4896.8 | 1070.9 | 846 | 777 | 407 | 1381 | 360 | 1103.8 | 638 | 11480.5 | 3482.8
14:00 | 4781.95 | 1037.9 | 886 | 787 | 441 | 1378.1 | 331 | 1122.8 | 641 | 11406.75 | 3472.9
15:00 | 5005.3 | 1026.1 | 899 | 725 | 435 | 1353 | 341 | 1098.4 | 617 | 11499.8 | 3409.4
16:00 | 5041.6 | 1044.5 | 904 | 797 | 433 | 1363.2 | 337 | 1127.4 | 609 | 11656.7 | 3436.6
17:00 | 4969.46 | 1122.2 | 873 | 789 | 409 | 1370 | 338 | 1058.2 | 602 | 11530.86 | 3368.2
18:00 | 4815.73 | 1158 | 1135 | 823 | 415 | 1323 | 315 | 1019 | 615 | 11618.73 | 3272
18:30 | 4759 | 1209.3 | 1206 | 877 | 506 | 1373 | 340 | 1041 | 672 | 11983.3 | 3426
19:00 | 4761.55 | 1250 | 1207 | 984 | 536 | 1682.5 | 427 | 1239.8 | 816 | 12903.85 | 4165.3
19:30 | 4763.7 | 1288.5 | 1116 | 998 | 535 | 1732 | 417 | 1333.6 | 861 | 13044.8 | 4343.6
20:00 | 4592.8 | 1299.7 | 1240 | 1022 | 525 | 1716 | 435 | 1344.6 | 870 | 13045.1 | 4365.6
21:00 | 4767.8 | 1349 | 1245 | 1030 | 501 | 1748 | 441 | 1369.8 | 855 | 13306.6 | 4413.8
22:00 | 4622.17 | 1317.5 | 1225 | 1003 | 515 | 1774.8 | 472 | 1325.6 | 828 | 13083.07 | 4400.4
23:00 | 4556.3 | 1194.5 | 986 | 879 | 540 | 1753.8 | 482 | 1306.6 | 784 | 12482.2 | 4326.4

## Min Gen W
Maximum Load: 11389.40 MW at 19:00 hrs.
Download
Hour | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total Load (MW) | W MW
0:00 | 3939.7 | 1024.2 | 936 | 683 | 397 | 1028.8 | 264 | 1209.8 | 660 | 10142.5 | 3162.6
1:00 | 3806.5 | 978.4 | 898 | 701 | 275 | 1021.8 | 260 | 1121.8 | 423 | 9485.5 | 2826.6
2:00 | 3658.52 | 963.2 | 880 | 689 | 301 | 997 | 255.8 | 1041 | 159 | 8944.52 | 2452.8
3:00 | 3558.8 | 863.4 | 850 | 637 | 320 | 942.4 | 245 | 543 | 85 | 8044.6 | 1815.4
4:00 | 3468.82 | 888.2 | 813 | 585 | 309 | 778.8 | 242 | 126.8 | 94 | 7305.62 | 1241.6
5:00 | 2879.4 | 812.8 | 790 | 307 | 295 | 534.7 | 231 | 168 | 127 | 6144.9 | 1060.7
6:00 | 1878 | 781.8 | 653 | 252 | 259 | 359.2 | 230 | 269 | 168 | 4850 | 1026.2
7:00 | 2528.62 | 851.2 | 262 | 275 | 257 | 333.6 | 117.2 | 362.3 | 228 | 5214.92 | 1041.1
8:00 | 2945.1 | 886.5 | 316 | 361 | 253 | 451.8 | 65.8 | 476.8 | 294 | 6050 | 1288.4
9:00 | 3411.8 | 792.5 | 438 | 409 | 162 | 577 | 74.8 | 604 | 356 | 6825.1 | 1611.8
10:00 | 3777.76 | 771.5 | 570 | 512 | 227 | 707 | 113.8 | 737 | 416 | 7832.06 | 1973.8
11:00 | 4069.3 | 743 | 644 | 563 | 304 | 843 | 141.4 | 824.4 | 444 | 8576.1 | 2252.8
12:00 | 4250.75 | 851.5 | 724 | 663 | 316 | 959.5 | 177 | 928.2 | 505 | 9374.95 | 2569.7
13:00 | 4079.1 | 914.5 | 749 | 683 | 316 | 1101 | 210.6 | 1022.8 | 531 | 9607 | 2865.4
14:00 | 4148.1 | 882 | 711 | 636 | 341 | 1109 | 224 | 986 | 534 | 9571.1 | 2853
15:00 | 4066.2 | 881.9 | 715 | 652 | 339 | 1071.2 | 232.4 | 995 | 479 | 9431.7 | 2777.6
16:00 | 4193.9 | 935.7 | 775 | 670 | 351 | 1088.4 | 229 | 1010 | 527 | 9780 | 2854.4
17:00 | 4214.1 | 977.4 | 840 | 772 | 344 | 1063.6 | 231 | 982 | 559 | 9983.1 | 2835.6
18:00 | 4217.2 | 1000.4 | 863 | 799 | 360 | 1132.6 | 244 | 983.2 | 616 | 10215.4 | 2975.8
18:30 | 4274.1 | 1052.8 | 985 | 858 | 411 | 1132.8 | 283 | 972.2 | 618 | 10586.9 | 3006
19:00 | 4459.2 | 1095 | 1047 | 927 | 446 | 1173.6 | 329 | 1156.6 | 756 | 11389.4 | 3415.2
19:30 | 4450.9 | 1033.9 | 1046 | 938 | 444 | 953 | 335 | 1237.6 | 765 | 11203.4 | 3290.6
20:00 | 4361 | 1071.2 | 1054 | 942 | 444 | 1036 | 340.4 | 1238.6 | 744 | 11231.2 | 3359
21:00 | 4280.1 | 1050 | 1062 | 932 | 434 | 1109.4 | 337 | 1265.6 | 721 | 11191.1 | 3433
22:00 | 4180.9 | 1010.3 | 1024 | 941 | 433 | 1184.8 | 320 | 1247.6 | 683 | 11024.6 | 3435.4
23:00 | 4098.7 | 979 | 1003 | 847 | 420 | 1183 | 300.6 | 1145.8 | 580 | 10557.1 | 3209.4

## Sheet1
date_time | grid_name | fuel_id | fuel_name | gen_mw
2023-05-01 | Eastern | 1 | Gas | 5050
2023-05-01 | Eastern | 2 | HFO | 1404
2023-05-01 | Eastern | 10 | Tripura | 144
2023-05-01 | Western | 1 | Gas | 1019
2023-05-01 | Western | 2 | HFO | 182
2023-05-01 | Western | 3 | HSD | 0
2023-05-01 | Western | 6 | Coal | 1831
2023-05-01 | Western | 8 | HVDC | 827
2023-05-01 01:00 | Eastern | 1 | Gas | 4871
2023-05-01 01:00 | Eastern | 2 | HFO | 1539
2023-05-01 01:00 | Eastern | 10 | Tripura | 148
2023-05-01 01:00 | Western | 1 | Gas | 1023
2023-05-01 01:00 | Western | 2 | HFO | 226
2023-05-01 01:00 | Western | 3 | HSD | 0
2023-05-01 01:00 | Western | 6 | Coal | 1865
2023-05-01 01:00 | Western | 8 | HVDC | 925
2023-05-01 02:00 | Eastern | 1 | Gas | 4852
2023-05-01 02:00 | Eastern | 2 | HFO | 1449.2
2023-05-01 02:00 | Eastern | 10 | Tripura | 146
2023-05-01 02:00 | Western | 1 | Gas | 1043
2023-05-01 02:00 | Western | 3 | HSD | 0
2023-05-01 02:00 | Western | 6 | Coal | 1826
2023-05-01 02:00 | Western | 8 | HVDC | 924
2023-05-01 03:00 | Eastern | 1 | Gas | 4871
2023-05-01 03:00 | Eastern | 2 | HFO | 1171.2
2023-05-01 03:00 | Eastern | 10 | Tripura | 142
2023-05-01 03:00 | Western | 1 | Gas | 1054
2023-05-01 03:00 | Western | 3 | HSD | 0
2023-05-01 03:00 | Western | 6 | Coal | 1776
2023-05-01 03:00 | Western | 8 | HVDC | 926
2023-05-01 04:00 | Eastern | 1 | Gas | 4828
2023-05-01 04:00 | Eastern | 2 | HFO | 1111.2
2023-05-01 04:00 | Eastern | 10 | Tripura | 140
2023-05-01 04:00 | Western | 1 | Gas | 1060
2023-05-01 04:00 | Western | 3 | HSD | 0
2023-05-01 04:00 | Western | 6 | Coal | 1533
2023-05-01 04:00 | Western | 8 | HVDC | 922
2023-05-01 05:00 | Eastern | 1 | Gas | 4774
2023-05-01 05:00 | Eastern | 2 | HFO | 1043.2
2023-05-01 05:00 | Eastern | 10 | Tripura | 132
2023-05-01 05:00 | Western | 1 | Gas | 1065
2023-05-01 05:00 | Western | 3 | HSD | 0
2023-05-01 05:00 | Western | 6 | Coal | 1431
2023-05-01 05:00 | Western | 8 | HVDC | 922
2023-05-01 06:00 | Eastern | 1 | Gas | 4546
2023-05-01 06:00 | Eastern | 2 | HFO | 937.2
2023-05-01 06:00 | Eastern | 10 | Tripura | 118
2023-05-01 06:00 | Eastern | 11 | Solar | 4
2023-05-01 06:00 | Western | 1 | Gas | 943
2023-05-01 06:00 | Western | 3 | HSD | 0
2023-05-01 06:00 | Western | 6 | Coal | 1285
2023-05-01 06:00 | Western | 8 | HVDC | 912
2023-05-01 06:00 | Western | 11 | Solar | 15.28
2023-05-01 07:00 | Eastern | 1 | Gas | 4584
2023-05-01 07:00 | Eastern | 2 | HFO | 810.2
2023-05-01 07:00 | Eastern | 10 | Tripura | 112
2023-05-01 07:00 | Eastern | 11 | Solar | 26
2023-05-01 07:00 | Western | 1 | Gas | 957
2023-05-01 07:00 | Western | 3 | HSD | 0
2023-05-01 07:00 | Western | 6 | Coal | 1276
2023-05-01 07:00 | Western | 8 | HVDC | 911
2023-05-01 07:00 | Western | 11 | Solar | 47.24
2023-05-01 08:00 | Eastern | 1 | Gas | 4401
2023-05-01 08:00 | Eastern | 2 | HFO | 569
2023-05-01 08:00 | Eastern | 10 | Tripura | 108
2023-05-01 08:00 | Eastern | 11 | Solar | 52
2023-05-01 08:00 | Western | 1 | Gas | 959
2023-05-01 08:00 | Western | 3 | HSD | 0
2023-05-01 08:00 | Western | 6 | Coal | 1254
2023-05-01 08:00 | Western | 8 | HVDC | 910
2023-05-01 08:00 | Western | 11 | Solar | 112.13
2023-05-01 09:00 | Eastern | 1 | Gas | 4368
2023-05-01 09:00 | Eastern | 2 | HFO | 569
2023-05-01 09:00 | Eastern | 10 | Tripura | 104
2023-05-01 09:00 | Eastern | 11 | Solar | 72
2023-05-01 09:00 | Western | 1 | Gas | 960
2023-05-01 09:00 | Western | 3 | HSD | 0
2023-05-01 09:00 | Western | 6 | Coal | 1269
2023-05-01 09:00 | Western | 8 | HVDC | 910
2023-05-01 09:00 | Western | 11 | Solar | 181.19
2023-05-01 10:00 | Eastern | 1 | Gas | 4456.5
2023-05-01 10:00 | Eastern | 2 | HFO | 653
2023-05-01 10:00 | Eastern | 5 | Hydro | 0
2023-05-01 10:00 | Eastern | 10 | Tripura | 108
2023-05-01 10:00 | Eastern | 11 | Solar | 90
2023-05-01 10:00 | Western | 1 | Gas | 929
2023-05-01 10:00 | Western | 3 | HSD | 0
2023-05-01 10:00 | Western | 6 | Coal | 1236
2023-05-01 10:00 | Western | 8 | HVDC | 910
2023-05-01 10:00 | Western | 11 | Solar | 213.55
2023-05-01 11:00 | Eastern | 1 | Gas | 4843
2023-05-01 11:00 | Eastern | 2 | HFO | 746
2023-05-01 11:00 | Eastern | 5 | Hydro | 25
2023-05-01 11:00 | Eastern | 10 | Tripura | 112
2023-05-01 11:00 | Eastern | 11 | Solar | 95
2023-05-01 11:00 | Western | 1 | Gas | 982
2023-05-01 11:00 | Western | 3 | HSD | 0
2023-05-01 11:00 | Western | 6 | Coal | 1221
2023-05-01 11:00 | Western | 8 | HVDC | 910
2023-05-01 11:00 | Western | 11 | Solar | 221.11
2023-05-01 12:00 | Eastern | 1 | Gas | 4978
2023-05-01 12:00 | Eastern | 2 | HFO | 848
2023-05-01 12:00 | Eastern | 5 | Hydro | 25
2023-05-01 12:00 | Eastern | 10 | Tripura | 120
2023-05-01 12:00 | Eastern | 11 | Solar | 104
2023-05-01 12:00 | Western | 1 | Gas | 1041
2023-05-01 12:00 | Western | 3 | HSD | 0
2023-05-01 12:00 | Western | 6 | Coal | 1253
2023-05-01 12:00 | Western | 8 | HVDC | 910
2023-05-01 12:00 | Western | 11 | Solar | 299.59
2023-05-01 13:00 | Eastern | 1 | Gas | 5274
2023-05-01 13:00 | Eastern | 2 | HFO | 819
2023-05-01 13:00 | Eastern | 5 | Hydro | 25
2023-05-01 13:00 | Eastern | 10 | Tripura | 128
2023-05-01 13:00 | Eastern | 11 | Solar | 97
2023-05-01 13:00 | Western | 1 | Gas | 1055
2023-05-01 13:00 | Western | 2 | HFO | 0
2023-05-01 13:00 | Western | 3 | HSD | 0
2023-05-01 13:00 | Western | 6 | Coal | 1409
2023-05-01 13:00 | Western | 8 | HVDC | 911
2023-05-01 13:00 | Western | 11 | Solar | 277.33
2023-05-01 14:00 | Eastern | 1 | Gas | 5249
2023-05-01 14:00 | Eastern | 2 | HFO | 1057
2023-05-01 14:00 | Eastern | 5 | Hydro | 25
2023-05-01 14:00 | Eastern | 10 | Tripura | 126
2023-05-01 14:00 | Eastern | 11 | Solar | 84
2023-05-01 14:00 | Western | 1 | Gas | 1112
2023-05-01 14:00 | Western | 2 | HFO | 67
2023-05-01 14:00 | Western | 3 | HSD | 0
2023-05-01 14:00 | Western | 6 | Coal | 1499.61
2023-05-01 14:00 | Western | 8 | HVDC | 912
2023-05-01 14:00 | Western | 11 | Solar | 128.57
2023-05-01 15:00 | Eastern | 1 | Gas | 5091
2023-05-01 15:00 | Eastern | 2 | HFO | 1192
2023-05-01 15:00 | Eastern | 5 | Hydro | 25
2023-05-01 15:00 | Eastern | 10 | Tripura | 128
2023-05-01 15:00 | Eastern | 11 | Solar | 54
2023-05-01 15:00 | Western | 1 | Gas | 1092
2023-05-01 15:00 | Western | 2 | HFO | 35
2023-05-01 15:00 | Western | 3 | HSD | 0
2023-05-01 15:00 | Western | 6 | Coal | 1472
2023-05-01 15:00 | Western | 8 | HVDC | 912
2023-05-01 15:00 | Western | 11 | Solar | 86.93
2023-05-01 16:00 | Eastern | 1 | Gas | 5110
2023-05-01 16:00 | Eastern | 2 | HFO | 1143
2023-05-01 16:00 | Eastern | 5 | Hydro | 25
2023-05-01 16:00 | Eastern | 10 | Tripura | 124
2023-05-01 16:00 | Eastern | 11 | Solar | 38
2023-05-01 16:00 | Western | 1 | Gas | 1055
2023-05-01 16:00 | Western | 2 | HFO | 0
2023-05-01 16:00 | Western | 3 | HSD | 0
2023-05-01 16:00 | Western | 6 | Coal | 1410
2023-05-01 16:00 | Western | 8 | HVDC | 906
2023-05-01 16:00 | Western | 11 | Solar | 52.36
2023-05-01 17:00 | Eastern | 1 | Gas | 4948
2023-05-01 17:00 | Eastern | 2 | HFO | 841
2023-05-01 17:00 | Eastern | 5 | Hydro | 25
2023-05-01 17:00 | Eastern | 10 | Tripura | 128
2023-05-01 17:00 | Eastern | 11 | Solar | 7
2023-05-01 17:00 | Western | 1 | Gas | 998
2023-05-01 17:00 | Western | 2 | HFO | 0
2023-05-01 17:00 | Western | 3 | HSD | 0
2023-05-01 17:00 | Western | 6 | Coal | 1287
2023-05-01 17:00 | Western | 8 | HVDC | 904
2023-05-01 17:00 | Western | 11 | Solar | 14.31
2023-05-01 18:00 | Eastern | 1 | Gas | 4851
2023-05-01 18:00 | Eastern | 2 | HFO | 978
2023-05-01 18:00 | Eastern | 5 | Hydro | 25
2023-05-01 18:00 | Eastern | 10 | Tripura | 124
2023-05-01 18:00 | Eastern | 11 | Solar | 1
2023-05-01 18:00 | Western | 1 | Gas | 979
2023-05-01 18:00 | Western | 2 | HFO | 12
2023-05-01 18:00 | Western | 3 | HSD | 0
2023-05-01 18:00 | Western | 6 | Coal | 1299
2023-05-01 18:00 | Western | 8 | HVDC | 904
2023-05-01 18:00 | Western | 11 | Solar | 3
2023-05-01 19:00 | Eastern | 1 | Gas | 5357
2023-05-01 19:00 | Eastern | 2 | HFO | 1398
2023-05-01 19:00 | Eastern | 5 | Hydro | 25
2023-05-01 19:00 | Eastern | 10 | Tripura | 148
2023-05-01 19:00 | Eastern | 11 | Solar | 0
2023-05-01 19:00 | Western | 1 | Gas | 999
2023-05-01 19:00 | Western | 2 | HFO | 93
2023-05-01 19:00 | Western | 3 | HSD | 0
2023-05-01 19:00 | Western | 6 | Coal | 1504
2023-05-01 19:00 | Western | 8 | HVDC | 904
2023-05-01 19:00 | Western | 11 | Solar | 0
2023-05-01 19:30 | Eastern | 1 | Gas | 5111
2023-05-01 19:30 | Eastern | 2 | HFO | 1787
2023-05-01 19:30 | Eastern | 5 | Hydro | 25
2023-05-01 19:30 | Eastern | 10 | Tripura | 130
2023-05-01 19:30 | Western | 1 | Gas | 988
2023-05-01 19:30 | Western | 2 | HFO | 191
2023-05-01 19:30 | Western | 3 | HSD | 0
2023-05-01 19:30 | Western | 6 | Coal | 1849.4
2023-05-01 19:30 | Western | 8 | HVDC | 904
2023-05-01 20:00 | Eastern | 1 | Gas | 5185
2023-05-01 20:00 | Eastern | 2 | HFO | 1679
2023-05-01 20:00 | Eastern | 5 | Hydro | 25
2023-05-01 20:00 | Eastern | 10 | Tripura | 142
2023-05-01 20:00 | Western | 1 | Gas | 1019
2023-05-01 20:00 | Western | 2 | HFO | 141
2023-05-01 20:00 | Western | 3 | HSD | 0
2023-05-01 20:00 | Western | 6 | Coal | 1877
2023-05-01 20:00 | Western | 8 | HVDC | 904
2023-05-01 21:00 | Eastern | 1 | Gas | 5339
2023-05-01 21:00 | Eastern | 2 | HFO | 1630
2023-05-01 21:00 | Eastern | 5 | Hydro | 25
2023-05-01 21:00 | Eastern | 10 | Tripura | 156
2023-05-01 21:00 | Western | 1 | Gas | 1052
2023-05-01 21:00 | Western | 2 | HFO | 240
2023-05-01 21:00 | Western | 3 | HSD | 0
2023-05-01 21:00 | Western | 6 | Coal | 1927
2023-05-01 21:00 | Western | 8 | HVDC | 905
2023-05-01 22:00 | Eastern | 1 | Gas | 5455
2023-05-01 22:00 | Eastern | 2 | HFO | 1517
2023-05-01 22:00 | Eastern | 5 | Hydro | 25
2023-05-01 22:00 | Eastern | 10 | Tripura | 158
2023-05-01 22:00 | Western | 1 | Gas | 1078
2023-05-01 22:00 | Western | 2 | HFO | 140
2023-05-01 22:00 | Western | 3 | HSD | 0
2023-05-01 22:00 | Western | 6 | Coal | 1928
2023-05-01 22:00 | Western | 8 | HVDC | 903
2023-05-01 23:00 | Eastern | 1 | Gas | 5520
2023-05-01 23:00 | Eastern | 2 | HFO | 1353
2023-05-01 23:00 | Eastern | 5 | Hydro | 0
2023-05-01 23:00 | Eastern | 10 | Tripura | 162
2023-05-01 23:00 | Western | 1 | Gas | 1081
2023-05-01 23:00 | Western | 2 | HFO | 105
2023-05-01 23:00 | Western | 3 | HSD | 0
2023-05-01 23:00 | Western | 6 | Coal | 1929
2023-05-01 23:00 | Western | 8 | HVDC | 903
2023-05-02 | Eastern | 1 | Gas | 5574
2023-05-02 | Eastern | 2 | HFO | 1113
2023-05-02 | Eastern | 3 | HSD | 0
2023-05-02 | Eastern | 10 | Tripura | 162
2023-05-02 | Western | 1 | Gas | 1082
2023-05-02 | Western | 2 | HFO | 35
2023-05-02 | Western | 3 | HSD | 0
2023-05-02 | Western | 6 | Coal | 1867
2023-05-02 | Western | 8 | HVDC | 903
2023-05-02 | Western | 11 | Solar | 0
2023-05-02 01:00 | Eastern | 1 | Gas | 5509
2023-05-02 01:00 | Eastern | 2 | HFO | 973
2023-05-02 01:00 | Eastern | 10 | Tripura | 156
2023-05-02 01:00 | Western | 1 | Gas | 1078
2023-05-02 01:00 | Western | 2 | HFO | 35
2023-05-02 01:00 | Western | 3 | HSD | 0
2023-05-02 01:00 | Western | 6 | Coal | 1766
2023-05-02 01:00 | Western | 8 | HVDC | 903
2023-05-02 02:00 | Eastern | 1 | Gas | 5426
2023-05-02 02:00 | Eastern | 2 | HFO | 838
2023-05-02 02:00 | Eastern | 10 | Tripura | 152
2023-05-02 02:00 | Western | 1 | Gas | 1079
2023-05-02 02:00 | Western | 3 | HSD | 0
2023-05-02 02:00 | Western | 6 | Coal | 1585
2023-05-02 02:00 | Western | 8 | HVDC | 903
2023-05-02 03:00 | Eastern | 1 | Gas | 5295
2023-05-02 03:00 | Eastern | 2 | HFO | 761
2023-05-02 03:00 | Eastern | 10 | Tripura | 150
2023-05-02 03:00 | Western | 1 | Gas | 1101
2023-05-02 03:00 | Western | 3 | HSD | 0
2023-05-02 03:00 | Western | 6 | Coal | 1486
2023-05-02 03:00 | Western | 8 | HVDC | 903
2023-05-02 04:00 | Eastern | 1 | Gas | 5192
2023-05-02 04:00 | Eastern | 2 | HFO | 755
2023-05-02 04:00 | Eastern | 10 | Tripura | 146
2023-05-02 04:00 | Western | 1 | Gas | 1083
2023-05-02 04:00 | Western | 3 | HSD | 0
2023-05-02 04:00 | Western | 6 | Coal | 1386
2023-05-02 04:00 | Western | 8 | HVDC | 903
2023-05-02 05:00 | Eastern | 1 | Gas | 5093
2023-05-02 05:00 | Eastern | 2 | HFO | 750
2023-05-02 05:00 | Eastern | 10 | Tripura | 142
2023-05-02 05:00 | Western | 1 | Gas | 1092
2023-05-02 05:00 | Western | 3 | HSD | 0
2023-05-02 05:00 | Western | 6 | Coal | 1384
2023-05-02 05:00 | Western | 8 | HVDC | 903
2023-05-02 06:00 | Eastern | 1 | Gas | 4972
2023-05-02 06:00 | Eastern | 2 | HFO | 720
2023-05-02 06:00 | Eastern | 10 | Tripura | 130
2023-05-02 06:00 | Eastern | 11 | Solar | 4
2023-05-02 06:00 | Western | 1 | Gas | 1088
2023-05-02 06:00 | Western | 3 | HSD | 0
2023-05-02 06:00 | Western | 6 | Coal | 1385
2023-05-02 06:00 | Western | 8 | HVDC | 903
2023-05-02 06:00 | Western | 11 | Solar | 10.22
2023-05-02 07:00 | Eastern | 1 | Gas | 5093
2023-05-02 07:00 | Eastern | 2 | HFO | 706
2023-05-02 07:00 | Eastern | 10 | Tripura | 130
2023-05-02 07:00 | Eastern | 11 | Solar | 21
2023-05-02 07:00 | Western | 1 | Gas | 1101
2023-05-02 07:00 | Western | 3 | HSD | 0
2023-05-02 07:00 | Western | 6 | Coal | 1425
2023-05-02 07:00 | Western | 8 | HVDC | 903
2023-05-02 07:00 | Western | 11 | Solar | 79.2
2023-05-02 08:00 | Eastern | 1 | Gas | 5198
2023-05-02 08:00 | Eastern | 2 | HFO | 738
2023-05-02 08:00 | Eastern | 10 | Tripura | 136
2023-05-02 08:00 | Eastern | 11 | Solar | 50
2023-05-02 08:00 | Western | 1 | Gas | 1081
2023-05-02 08:00 | Western | 3 | HSD | 0
2023-05-02 08:00 | Western | 6 | Coal | 1487
2023-05-02 08:00 | Western | 8 | HVDC | 903
2023-05-02 08:00 | Western | 11 | Solar | 166.77
2023-05-02 09:00 | Eastern | 1 | Gas | 5244
2023-05-02 09:00 | Eastern | 2 | HFO | 896
2023-05-02 09:00 | Eastern | 5 | Hydro | 0
2023-05-02 09:00 | Eastern | 10 | Tripura | 140
2023-05-02 09:00 | Eastern | 11 | Solar | 66
2023-05-02 09:00 | Western | 1 | Gas | 1060
2023-05-02 09:00 | Western | 3 | HSD | 0
2023-05-02 09:00 | Western | 6 | Coal | 1604
2023-05-02 09:00 | Western | 8 | HVDC | 903
2023-05-02 09:00 | Western | 11 | Solar | 201.17
2023-05-02 10:00 | Eastern | 1 | Gas | 5024
2023-05-02 10:00 | Eastern | 2 | HFO | 1286
2023-05-02 10:00 | Eastern | 3 | HSD | 92
2023-05-02 10:00 | Eastern | 5 | Hydro | 25
2023-05-02 10:00 | Eastern | 10 | Tripura | 146
2023-05-02 10:00 | Eastern | 11 | Solar | 97
2023-05-02 10:00 | Western | 1 | Gas | 1011
2023-05-02 10:00 | Western | 2 | HFO | 161
2023-05-02 10:00 | Western | 3 | HSD | 0
2023-05-02 10:00 | Western | 6 | Coal | 1707
2023-05-02 10:00 | Western | 8 | HVDC | 903
2023-05-02 10:00 | Western | 11 | Solar | 305.31
2023-05-02 11:00 | Eastern | 1 | Gas | 5064
2023-05-02 11:00 | Eastern | 2 | HFO | 1860
2023-05-02 11:00 | Eastern | 5 | Hydro | 25
2023-05-02 11:00 | Eastern | 10 | Tripura | 152
2023-05-02 11:00 | Eastern | 11 | Solar | 98
2023-05-02 11:00 | Western | 1 | Gas | 966
2023-05-02 11:00 | Western | 2 | HFO | 211
2023-05-02 11:00 | Western | 3 | HSD | 0
2023-05-02 11:00 | Western | 6 | Coal | 1816
2023-05-02 11:00 | Western | 8 | HVDC | 902
2023-05-02 11:00 | Western | 11 | Solar | 340.64
2023-05-02 12:00 | Eastern | 1 | Gas | 5318
2023-05-02 12:00 | Eastern | 2 | HFO | 2041
2023-05-02 12:00 | Eastern | 5 | Hydro | 25
2023-05-02 12:00 | Eastern | 10 | Tripura | 158
2023-05-02 12:00 | Eastern | 11 | Solar | 104
2023-05-02 12:00 | Western | 1 | Gas | 902
2023-05-02 12:00 | Western | 2 | HFO | 281
2023-05-02 12:00 | Western | 3 | HSD | 0
2023-05-02 12:00 | Western | 6 | Coal | 1825
2023-05-02 12:00 | Western | 8 | HVDC | 903
2023-05-02 12:00 | Western | 11 | Solar | 276.43
2023-05-02 13:00 | Eastern | 1 | Gas | 5197
2023-05-02 13:00 | Eastern | 2 | HFO | 2237
2023-05-02 13:00 | Eastern | 5 | Hydro | 25
2023-05-02 13:00 | Eastern | 10 | Tripura | 160
2023-05-02 13:00 | Eastern | 11 | Solar | 103
2023-05-02 13:00 | Western | 1 | Gas | 861
2023-05-02 13:00 | Western | 2 | HFO | 499.28
2023-05-02 13:00 | Western | 3 | HSD | 0
2023-05-02 13:00 | Western | 6 | Coal | 1924
2023-05-02 13:00 | Western | 8 | HVDC | 909
2023-05-02 13:00 | Western | 11 | Solar | 267.7
2023-05-02 14:00 | Eastern | 1 | Gas | 5039
2023-05-02 14:00 | Eastern | 2 | HFO | 2195
2023-05-02 14:00 | Eastern | 5 | Hydro | 25
2023-05-02 14:00 | Eastern | 10 | Tripura | 164
2023-05-02 14:00 | Eastern | 11 | Solar | 92
2023-05-02 14:00 | Western | 1 | Gas | 802
2023-05-02 14:00 | Western | 2 | HFO | 545
2023-05-02 14:00 | Western | 3 | HSD | 0
2023-05-02 14:00 | Western | 6 | Coal | 1867
2023-05-02 14:00 | Western | 8 | HVDC | 913
2023-05-02 14:00 | Western | 11 | Solar | 217.83
2023-05-02 15:00 | Eastern | 1 | Gas | 5195
2023-05-02 15:00 | Eastern | 2 | HFO | 2205
2023-05-02 15:00 | Eastern | 5 | Hydro | 25
2023-05-02 15:00 | Eastern | 10 | Tripura | 170
2023-05-02 15:00 | Eastern | 11 | Solar | 67
2023-05-02 15:00 | Western | 1 | Gas | 828
2023-05-02 15:00 | Western | 2 | HFO | 587
2023-05-02 15:00 | Western | 3 | HSD | 0
2023-05-02 15:00 | Western | 6 | Coal | 1913
2023-05-02 15:00 | Western | 8 | HVDC | 914
2023-05-02 15:00 | Western | 11 | Solar | 210.83
2023-05-02 16:00 | Eastern | 1 | Gas | 5179
2023-05-02 16:00 | Eastern | 2 | HFO | 2252
2023-05-02 16:00 | Eastern | 5 | Hydro | 25
2023-05-02 16:00 | Eastern | 10 | Tripura | 164
2023-05-02 16:00 | Eastern | 11 | Solar | 50
2023-05-02 16:00 | Western | 1 | Gas | 830
2023-05-02 16:00 | Western | 2 | HFO | 544
2023-05-02 16:00 | Western | 3 | HSD | 0
2023-05-02 16:00 | Western | 6 | Coal | 1888
2023-05-02 16:00 | Western | 8 | HVDC | 908
2023-05-02 16:00 | Western | 11 | Solar | 100.8
2023-05-02 17:00 | Eastern | 1 | Gas | 5113
2023-05-02 17:00 | Eastern | 2 | HFO | 2359
2023-05-02 17:00 | Eastern | 5 | Hydro | 25
2023-05-02 17:00 | Eastern | 10 | Tripura | 164
2023-05-02 17:00 | Eastern | 11 | Solar | 22
2023-05-02 17:00 | Western | 1 | Gas | 808
2023-05-02 17:00 | Western | 2 | HFO | 495
2023-05-02 17:00 | Western | 3 | HSD | 0
2023-05-02 17:00 | Western | 6 | Coal | 1798
2023-05-02 17:00 | Western | 8 | HVDC | 898
2023-05-02 17:00 | Western | 11 | Solar | 36.56
2023-05-02 18:00 | Eastern | 1 | Gas | 4688
2023-05-02 18:00 | Eastern | 2 | HFO | 2515
2023-05-02 18:00 | Eastern | 5 | Hydro | 25
2023-05-02 18:00 | Eastern | 10 | Tripura | 156
2023-05-02 18:00 | Eastern | 11 | Solar | 3
2023-05-02 18:00 | Western | 1 | Gas | 850
2023-05-02 18:00 | Western | 2 | HFO | 501
2023-05-02 18:00 | Western | 3 | HSD | 0
2023-05-02 18:00 | Western | 6 | Coal | 1404
2023-05-02 18:00 | Western | 8 | HVDC | 899
2023-05-02 18:00 | Western | 11 | Solar | 5.09
2023-05-02 19:00 | Eastern | 1 | Gas | 5266
2023-05-02 19:00 | Eastern | 2 | HFO | 3056
2023-05-02 19:00 | Eastern | 5 | Hydro | 25
2023-05-02 19:00 | Eastern | 10 | Tripura | 166
2023-05-02 19:00 | Eastern | 11 | Solar | 0
2023-05-02 19:00 | Western | 1 | Gas | 881
2023-05-02 19:00 | Western | 2 | HFO | 888
2023-05-02 19:00 | Western | 3 | HSD | 0
2023-05-02 19:00 | Western | 6 | Coal | 1447
2023-05-02 19:00 | Western | 8 | HVDC | 898
2023-05-02 19:00 | Western | 11 | Solar | 1
2023-05-02 19:30 | Eastern | 1 | Gas | 5366.79
2023-05-02 19:30 | Eastern | 2 | HFO | 3187
2023-05-02 19:30 | Eastern | 5 | Hydro | 25
2023-05-02 19:30 | Eastern | 10 | Tripura | 168
2023-05-02 19:30 | Western | 1 | Gas | 914
2023-05-02 19:30 | Western | 2 | HFO | 1046
2023-05-02 19:30 | Western | 3 | HSD | 0
2023-05-02 19:30 | Western | 6 | Coal | 1725
2023-05-02 19:30 | Western | 8 | HVDC | 899
2023-05-02 19:30 | Western | 11 | Solar | 0
2023-05-02 20:00 | Eastern | 1 | Gas | 5239.79
2023-05-02 20:00 | Eastern | 2 | HFO | 3275
2023-05-02 20:00 | Eastern | 5 | Hydro | 25
2023-05-02 20:00 | Eastern | 10 | Tripura | 168
2023-05-02 20:00 | Western | 1 | Gas | 906
2023-05-02 20:00 | Western | 2 | HFO | 1029
2023-05-02 20:00 | Western | 3 | HSD | 0
2023-05-02 20:00 | Western | 6 | Coal | 1754
2023-05-02 20:00 | Western | 8 | HVDC | 899
2023-05-02 21:00 | Eastern | 1 | Gas | 5327.79
2023-05-02 21:00 | Eastern | 2 | HFO | 3035
2023-05-02 21:00 | Eastern | 5 | Hydro | 25
2023-05-02 21:00 | Eastern | 10 | Tripura | 164
2023-05-02 21:00 | Western | 1 | Gas | 931
2023-05-02 21:00 | Western | 2 | HFO | 988
2023-05-02 21:00 | Western | 3 | HSD | 0
2023-05-02 21:00 | Western | 6 | Coal | 1968
2023-05-02 21:00 | Western | 8 | HVDC | 898
2023-05-02 22:00 | Eastern | 1 | Gas | 5313.79
2023-05-02 22:00 | Eastern | 2 | HFO | 2943.2
2023-05-02 22:00 | Eastern | 5 | Hydro | 25
2023-05-02 22:00 | Eastern | 10 | Tripura | 172
2023-05-02 22:00 | Western | 1 | Gas | 949
2023-05-02 22:00 | Western | 2 | HFO | 809
2023-05-02 22:00 | Western | 3 | HSD | 0
2023-05-02 22:00 | Western | 6 | Coal | 1982
2023-05-02 22:00 | Western | 8 | HVDC | 898
2023-05-02 23:00 | Eastern | 1 | Gas | 5419.79
2023-05-02 23:00 | Eastern | 2 | HFO | 2564.2
2023-05-02 23:00 | Eastern | 5 | Hydro | 0
2023-05-02 23:00 | Eastern | 10 | Tripura | 176
2023-05-02 23:00 | Western | 1 | Gas | 937
2023-05-02 23:00 | Western | 2 | HFO | 870
2023-05-02 23:00 | Western | 3 | HSD | 0
2023-05-02 23:00 | Western | 6 | Coal | 1970.69
2023-05-02 23:00 | Western | 8 | HVDC | 899
2023-05-03 | Eastern | 1 | Gas | 5352.79
2023-05-03 | Eastern | 2 | HFO | 2130.2
2023-05-03 | Eastern | 3 | HSD | 0
2023-05-03 | Eastern | 10 | Tripura | 174
2023-05-03 | Eastern | 11 | Solar | 0
2023-05-03 | Western | 1 | Gas | 936
2023-05-03 | Western | 2 | HFO | 1038
2023-05-03 | Western | 3 | HSD | 0
2023-05-03 | Western | 6 | Coal | 1975
2023-05-03 | Western | 8 | HVDC | 899
2023-05-03 01:00 | Eastern | 1 | Gas | 5226
2023-05-03 01:00 | Eastern | 2 | HFO | 1791.2
2023-05-03 01:00 | Eastern | 10 | Tripura | 170
2023-05-03 01:00 | Western | 1 | Gas | 935
2023-05-03 01:00 | Western | 2 | HFO | 946
2023-05-03 01:00 | Western | 3 | HSD | 0
2023-05-03 01:00 | Western | 6 | Coal | 1966
2023-05-03 01:00 | Western | 8 | HVDC | 932
2023-05-03 02:00 | Eastern | 1 | Gas | 5141
2023-05-03 02:00 | Eastern | 2 | HFO | 1628.2
2023-05-03 02:00 | Eastern | 10 | Tripura | 166
2023-05-03 02:00 | Western | 1 | Gas | 929
2023-05-03 02:00 | Western | 2 | HFO | 782
2023-05-03 02:00 | Western | 3 | HSD | 0
2023-05-03 02:00 | Western | 6 | Coal | 1982
2023-05-03 02:00 | Western | 8 | HVDC | 898
2023-05-03 03:00 | Eastern | 1 | Gas | 5208
2023-05-03 03:00 | Eastern | 2 | HFO | 1643.2
2023-05-03 03:00 | Eastern | 10 | Tripura | 166
2023-05-03 03:00 | Western | 1 | Gas | 930
2023-05-03 03:00 | Western | 2 | HFO | 498
2023-05-03 03:00 | Western | 3 | HSD | 0
2023-05-03 03:00 | Western | 6 | Coal | 1982
2023-05-03 03:00 | Western | 8 | HVDC | 900
2023-05-03 04:00 | Eastern | 1 | Gas | 5222
2023-05-03 04:00 | Eastern | 2 | HFO | 1508.2
2023-05-03 04:00 | Eastern | 10 | Tripura | 160
2023-05-03 04:00 | Western | 1 | Gas | 934
2023-05-03 04:00 | Western | 2 | HFO | 322
2023-05-03 04:00 | Western | 3 | HSD | 0
2023-05-03 04:00 | Western | 6 | Coal | 1983.5
2023-05-03 04:00 | Western | 8 | HVDC | 900
2023-05-03 05:00 | Eastern | 1 | Gas | 5234
2023-05-03 05:00 | Eastern | 2 | HFO | 1495.2
2023-05-03 05:00 | Eastern | 10 | Tripura | 158
2023-05-03 05:00 | Eastern | 11 | Solar | 0
2023-05-03 05:00 | Western | 1 | Gas | 934
2023-05-03 05:00 | Western | 2 | HFO | 212.5
2023-05-03 05:00 | Western | 3 | HSD | 0
2023-05-03 05:00 | Western | 6 | Coal | 1984
2023-05-03 05:00 | Western | 8 | HVDC | 902
2023-05-03 05:00 | Western | 11 | Solar | 0
2023-05-03 06:00 | Eastern | 1 | Gas | 5074
2023-05-03 06:00 | Eastern | 2 | HFO | 1416
2023-05-03 06:00 | Eastern | 10 | Tripura | 143
2023-05-03 06:00 | Eastern | 11 | Solar | 6
2023-05-03 06:00 | Western | 1 | Gas | 926
2023-05-03 06:00 | Western | 2 | HFO | 163.7
2023-05-03 06:00 | Western | 3 | HSD | 0
2023-05-03 06:00 | Western | 6 | Coal | 1977
2023-05-03 06:00 | Western | 8 | HVDC | 902
2023-05-03 06:00 | Western | 11 | Solar | 11.14
2023-05-03 07:00 | Eastern | 1 | Gas | 5132
2023-05-03 07:00 | Eastern | 2 | HFO | 1370
2023-05-03 07:00 | Eastern | 10 | Tripura | 142
2023-05-03 07:00 | Eastern | 11 | Solar | 15
2023-05-03 07:00 | Western | 1 | Gas | 916
2023-05-03 07:00 | Western | 2 | HFO | 163.7
2023-05-03 07:00 | Western | 3 | HSD | 0
2023-05-03 07:00 | Western | 6 | Coal | 1972
2023-05-03 07:00 | Western | 8 | HVDC | 902
2023-05-03 07:00 | Western | 11 | Solar | 46.9
2023-05-03 08:00 | Eastern | 1 | Gas | 4981
2023-05-03 08:00 | Eastern | 2 | HFO | 1373
2023-05-03 08:00 | Eastern | 10 | Tripura | 144
2023-05-03 08:00 | Eastern | 11 | Solar | 41
2023-05-03 08:00 | Western | 1 | Gas | 918
2023-05-03 08:00 | Western | 2 | HFO | 243.7
2023-05-03 08:00 | Western | 3 | HSD | 0
2023-05-03 08:00 | Western | 6 | Coal | 1971
2023-05-03 08:00 | Western | 8 | HVDC | 902
2023-05-03 08:00 | Western | 11 | Solar | 131.46
2023-05-03 09:00 | Eastern | 1 | Gas | 5089.5
2023-05-03 09:00 | Eastern | 2 | HFO | 1504
2023-05-03 09:00 | Eastern | 10 | Tripura | 144
2023-05-03 09:00 | Eastern | 11 | Solar | 59
2023-05-03 09:00 | Western | 1 | Gas | 919
2023-05-03 09:00 | Western | 2 | HFO | 386.7
2023-05-03 09:00 | Western | 3 | HSD | 0
2023-05-03 09:00 | Western | 6 | Coal | 1936
2023-05-03 09:00 | Western | 8 | HVDC | 902
2023-05-03 09:00 | Western | 11 | Solar | 168.17
2023-05-03 10:00 | Eastern | 1 | Gas | 5100
2023-05-03 10:00 | Eastern | 2 | HFO | 2018
2023-05-03 10:00 | Eastern | 3 | HSD | 149
2023-05-03 10:00 | Eastern | 5 | Hydro | 0
2023-05-03 10:00 | Eastern | 10 | Tripura | 152
2023-05-03 10:00 | Eastern | 11 | Solar | 76
2023-05-03 10:00 | Western | 1 | Gas | 912
2023-05-03 10:00 | Western | 2 | HFO | 369
2023-05-03 10:00 | Western | 3 | HSD | 0
2023-05-03 10:00 | Western | 6 | Coal | 1914
2023-05-03 10:00 | Western | 8 | HVDC | 902
2023-05-03 10:00 | Western | 11 | Solar | 257.01
2023-05-03 11:00 | Eastern | 1 | Gas | 5129
2023-05-03 11:00 | Eastern | 2 | HFO | 2303
2023-05-03 11:00 | Eastern | 3 | HSD | 12
2023-05-03 11:00 | Eastern | 5 | Hydro | 25
2023-05-03 11:00 | Eastern | 10 | Tripura | 158
2023-05-03 11:00 | Eastern | 11 | Solar | 83
2023-05-03 11:00 | Western | 1 | Gas | 922
2023-05-03 11:00 | Western | 2 | HFO | 496
2023-05-03 11:00 | Western | 3 | HSD | 0
2023-05-03 11:00 | Western | 6 | Coal | 1962
2023-05-03 11:00 | Western | 8 | HVDC | 901
2023-05-03 11:00 | Western | 11 | Solar | 252.71
2023-05-03 12:00 | Eastern | 1 | Gas | 5071
2023-05-03 12:00 | Eastern | 2 | HFO | 2499
2023-05-03 12:00 | Eastern | 3 | HSD | 179
2023-05-03 12:00 | Eastern | 5 | Hydro | 25
2023-05-03 12:00 | Eastern | 10 | Tripura | 164
2023-05-03 12:00 | Eastern | 11 | Solar | 86
2023-05-03 12:00 | Western | 1 | Gas | 897
2023-05-03 12:00 | Western | 2 | HFO | 565
2023-05-03 12:00 | Western | 3 | HSD | 0
2023-05-03 12:00 | Western | 6 | Coal | 1980
2023-05-03 12:00 | Western | 8 | HVDC | 901
2023-05-03 12:00 | Western | 11 | Solar | 231
2023-05-03 13:00 | Eastern | 1 | Gas | 5067.5
2023-05-03 13:00 | Eastern | 2 | HFO | 2492
2023-05-03 13:00 | Eastern | 3 | HSD | 342
2023-05-03 13:00 | Eastern | 5 | Hydro | 25
2023-05-03 13:00 | Eastern | 10 | Tripura | 168
2023-05-03 13:00 | Eastern | 11 | Solar | 71
2023-05-03 13:00 | Western | 1 | Gas | 881
2023-05-03 13:00 | Western | 2 | HFO | 694
2023-05-03 13:00 | Western | 3 | HSD | 0
2023-05-03 13:00 | Western | 6 | Coal | 1975
2023-05-03 13:00 | Western | 8 | HVDC | 905
2023-05-03 13:00 | Western | 11 | Solar | 278.21
2023-05-03 14:00 | Eastern | 1 | Gas | 4882.5
2023-05-03 14:00 | Eastern | 2 | HFO | 2255
2023-05-03 14:00 | Eastern | 3 | HSD | 433
2023-05-03 14:00 | Eastern | 5 | Hydro | 25
2023-05-03 14:00 | Eastern | 10 | Tripura | 172
2023-05-03 14:00 | Eastern | 11 | Solar | 39
2023-05-03 14:00 | Western | 1 | Gas | 858
2023-05-03 14:00 | Western | 2 | HFO | 720
2023-05-03 14:00 | Western | 3 | HSD | 0
2023-05-03 14:00 | Western | 6 | Coal | 1878
2023-05-03 14:00 | Western | 8 | HVDC | 904
2023-05-03 14:00 | Western | 11 | Solar | 272.21
2023-05-03 15:00 | Eastern | 1 | Gas | 4664
2023-05-03 15:00 | Eastern | 2 | HFO | 2105
2023-05-03 15:00 | Eastern | 5 | Hydro | 25
2023-05-03 15:00 | Eastern | 10 | Tripura | 174
2023-05-03 15:00 | Eastern | 11 | Solar | 74
2023-05-03 15:00 | Western | 1 | Gas | 852
2023-05-03 15:00 | Western | 2 | HFO | 587
2023-05-03 15:00 | Western | 3 | HSD | 0
2023-05-03 15:00 | Western | 6 | Coal | 1861
2023-05-03 15:00 | Western | 8 | HVDC | 904
2023-05-03 15:00 | Western | 11 | Solar | 200.14
2023-05-03 16:00 | Eastern | 1 | Gas | 4769
2023-05-03 16:00 | Eastern | 2 | HFO | 1943
2023-05-03 16:00 | Eastern | 5 | Hydro | 25
2023-05-03 16:00 | Eastern | 10 | Tripura | 164
2023-05-03 16:00 | Eastern | 11 | Solar | 32
2023-05-03 16:00 | Western | 1 | Gas | 842
2023-05-03 16:00 | Western | 2 | HFO | 553
2023-05-03 16:00 | Western | 3 | HSD | 0
2023-05-03 16:00 | Western | 6 | Coal | 1881
2023-05-03 16:00 | Western | 8 | HVDC | 904
2023-05-03 16:00 | Western | 11 | Solar | 129.47
2023-05-03 17:00 | Eastern | 1 | Gas | 4652
2023-05-03 17:00 | Eastern | 2 | HFO | 2036
2023-05-03 17:00 | Eastern | 5 | Hydro | 25
2023-05-03 17:00 | Eastern | 10 | Tripura | 150
2023-05-03 17:00 | Eastern | 11 | Solar | 10
2023-05-03 17:00 | Western | 1 | Gas | 835
2023-05-03 17:00 | Western | 2 | HFO | 499
2023-05-03 17:00 | Western | 3 | HSD | 0
2023-05-03 17:00 | Western | 6 | Coal | 1771
2023-05-03 17:00 | Western | 8 | HVDC | 904
2023-05-03 17:00 | Western | 11 | Solar | 40.64
2023-05-03 18:00 | Eastern | 1 | Gas | 4325
2023-05-03 18:00 | Eastern | 2 | HFO | 2143
2023-05-03 18:00 | Eastern | 5 | Hydro | 25
2023-05-03 18:00 | Eastern | 10 | Tripura | 150
2023-05-03 18:00 | Eastern | 11 | Solar | 2
2023-05-03 18:00 | Western | 1 | Gas | 823
2023-05-03 18:00 | Western | 2 | HFO | 538
2023-05-03 18:00 | Western | 3 | HSD | 0
2023-05-03 18:00 | Western | 6 | Coal | 1772
2023-05-03 18:00 | Western | 8 | HVDC | 903
2023-05-03 18:00 | Western | 11 | Solar | 10.06
2023-05-03 19:00 | Eastern | 1 | Gas | 4536
2023-05-03 19:00 | Eastern | 2 | HFO | 2874
2023-05-03 19:00 | Eastern | 5 | Hydro | 25
2023-05-03 19:00 | Eastern | 10 | Tripura | 116
2023-05-03 19:00 | Western | 1 | Gas | 802
2023-05-03 19:00 | Western | 2 | HFO | 758
2023-05-03 19:00 | Western | 3 | HSD | 0
2023-05-03 19:00 | Western | 6 | Coal | 1825
2023-05-03 19:00 | Western | 8 | HVDC | 903
2023-05-03 19:30 | Eastern | 1 | Gas | 4712
2023-05-03 19:30 | Eastern | 2 | HFO | 2914
2023-05-03 19:30 | Eastern | 5 | Hydro | 25
2023-05-03 19:30 | Eastern | 10 | Tripura | 138
2023-05-03 19:30 | Western | 1 | Gas | 843
2023-05-03 19:30 | Western | 2 | HFO | 856
2023-05-03 19:30 | Western | 3 | HSD | 0
2023-05-03 19:30 | Western | 6 | Coal | 1945
2023-05-03 19:30 | Western | 8 | HVDC | 856
2023-05-03 20:00 | Eastern | 1 | Gas | 4889
2023-05-03 20:00 | Eastern | 2 | HFO | 2860
2023-05-03 20:00 | Eastern | 5 | Hydro | 25
2023-05-03 20:00 | Eastern | 10 | Tripura | 146
2023-05-03 20:00 | Western | 1 | Gas | 859
2023-05-03 20:00 | Western | 2 | HFO | 712
2023-05-03 20:00 | Western | 3 | HSD | 0
2023-05-03 20:00 | Western | 6 | Coal | 1963
2023-05-03 20:00 | Western | 8 | HVDC | 833
2023-05-03 21:00 | Eastern | 1 | Gas | 4942
2023-05-03 21:00 | Eastern | 2 | HFO | 2746
2023-05-03 21:00 | Eastern | 5 | Hydro | 25
2023-05-03 21:00 | Eastern | 10 | Tripura | 144
2023-05-03 21:00 | Western | 1 | Gas | 890
2023-05-03 21:00 | Western | 2 | HFO | 814
2023-05-03 21:00 | Western | 3 | HSD | 0
2023-05-03 21:00 | Western | 6 | Coal | 1973
2023-05-03 21:00 | Western | 8 | HVDC | 832
2023-05-03 22:00 | Eastern | 1 | Gas | 4830
2023-05-03 22:00 | Eastern | 2 | HFO | 2607
2023-05-03 22:00 | Eastern | 5 | Hydro | 25
2023-05-03 22:00 | Eastern | 10 | Tripura | 148
2023-05-03 22:00 | Western | 1 | Gas | 915
2023-05-03 22:00 | Western | 2 | HFO | 776
2023-05-03 22:00 | Western | 3 | HSD | 0
2023-05-03 22:00 | Western | 6 | Coal | 1973
2023-05-03 22:00 | Western | 8 | HVDC | 905
2023-05-03 23:00 | Eastern | 1 | Gas | 4976
2023-05-03 23:00 | Eastern | 2 | HFO | 2353
2023-05-03 23:00 | Eastern | 10 | Tripura | 150
2023-05-03 23:00 | Western | 1 | Gas | 924
2023-05-03 23:00 | Western | 2 | HFO | 724
2023-05-03 23:00 | Western | 3 | HSD | 0
2023-05-03 23:00 | Western | 6 | Coal | 1974
2023-05-03 23:00 | Western | 8 | HVDC | 905
2023-05-04 | Eastern | 1 | Gas | 5027
2023-05-04 | Eastern | 2 | HFO | 1866
2023-05-04 | Eastern | 10 | Tripura | 146
2023-05-04 | Eastern | 11 | Solar | 0
2023-05-04 | Western | 1 | Gas | 929
2023-05-04 | Western | 2 | HFO | 730
2023-05-04 | Western | 3 | HSD | 0
2023-05-04 | Western | 6 | Coal | 1979
2023-05-04 | Western | 8 | HVDC | 905
2023-05-04 01:00 | Eastern | 1 | Gas | 4998
2023-05-04 01:00 | Eastern | 2 | HFO | 1627
2023-05-04 01:00 | Eastern | 10 | Tripura | 140
2023-05-04 01:00 | Western | 1 | Gas | 927
2023-05-04 01:00 | Western | 2 | HFO | 647
2023-05-04 01:00 | Western | 3 | HSD | 0
2023-05-04 01:00 | Western | 6 | Coal | 1978
2023-05-04 01:00 | Western | 8 | HVDC | 905
2023-05-04 02:00 | Eastern | 1 | Gas | 4956
2023-05-04 02:00 | Eastern | 2 | HFO | 1458
2023-05-04 02:00 | Eastern | 10 | Tripura | 136
2023-05-04 02:00 | Western | 1 | Gas | 930
2023-05-04 02:00 | Western | 2 | HFO | 541
2023-05-04 02:00 | Western | 3 | HSD | 0
2023-05-04 02:00 | Western | 6 | Coal | 1981
2023-05-04 02:00 | Western | 8 | HVDC | 904
2023-05-04 03:00 | Eastern | 1 | Gas | 4967
2023-05-04 03:00 | Eastern | 2 | HFO | 1401.2
2023-05-04 03:00 | Eastern | 10 | Tripura | 134
2023-05-04 03:00 | Western | 1 | Gas | 945
2023-05-04 03:00 | Western | 2 | HFO | 359
2023-05-04 03:00 | Western | 3 | HSD | 0
2023-05-04 03:00 | Western | 6 | Coal | 1980
2023-05-04 03:00 | Western | 8 | HVDC | 903
2023-05-04 04:00 | Eastern | 1 | Gas | 4962
2023-05-04 04:00 | Eastern | 2 | HFO | 1300.2
2023-05-04 04:00 | Eastern | 10 | Tripura | 132
2023-05-04 04:00 | Western | 1 | Gas | 948
2023-05-04 04:00 | Western | 2 | HFO | 243
2023-05-04 04:00 | Western | 3 | HSD | 0
2023-05-04 04:00 | Western | 6 | Coal | 1890
2023-05-04 04:00 | Western | 8 | HVDC | 903
2023-05-04 05:00 | Eastern | 1 | Gas | 4846
2023-05-04 05:00 | Eastern | 2 | HFO | 1238.2
2023-05-04 05:00 | Eastern | 10 | Tripura | 130
2023-05-04 05:00 | Western | 1 | Gas | 968
2023-05-04 05:00 | Western | 2 | HFO | 243
2023-05-04 05:00 | Western | 3 | HSD | 0
2023-05-04 05:00 | Western | 6 | Coal | 1837
2023-05-04 05:00 | Western | 8 | HVDC | 903
2023-05-04 06:00 | Eastern | 1 | Gas | 4715
2023-05-04 06:00 | Eastern | 2 | HFO | 1190.2
2023-05-04 06:00 | Eastern | 10 | Tripura | 116
2023-05-04 06:00 | Eastern | 11 | Solar | 2
2023-05-04 06:00 | Western | 1 | Gas | 960
2023-05-04 06:00 | Western | 2 | HFO | 195
2023-05-04 06:00 | Western | 3 | HSD | 0
2023-05-04 06:00 | Western | 6 | Coal | 1674
2023-05-04 06:00 | Western | 8 | HVDC | 904
2023-05-04 06:00 | Western | 11 | Solar | 6.16
2023-05-04 07:00 | Eastern | 1 | Gas | 4751
2023-05-04 07:00 | Eastern | 2 | HFO | 1170.2
2023-05-04 07:00 | Eastern | 10 | Tripura | 112
2023-05-04 07:00 | Eastern | 11 | Solar | 10
2023-05-04 07:00 | Western | 1 | Gas | 955
2023-05-04 07:00 | Western | 2 | HFO | 195
2023-05-04 07:00 | Western | 3 | HSD | 0
2023-05-04 07:00 | Western | 6 | Coal | 1691
2023-05-04 07:00 | Western | 8 | HVDC | 904
2023-05-04 07:00 | Western | 11 | Solar | 18.62
2023-05-04 08:00 | Eastern | 1 | Gas | 4709
2023-05-04 08:00 | Eastern | 2 | HFO | 1092.2
2023-05-04 08:00 | Eastern | 10 | Tripura | 120
2023-05-04 08:00 | Eastern | 11 | Solar | 33
2023-05-04 08:00 | Western | 1 | Gas | 937
2023-05-04 08:00 | Western | 2 | HFO | 195
2023-05-04 08:00 | Western | 3 | HSD | 0
2023-05-04 08:00 | Western | 6 | Coal | 1797
2023-05-04 08:00 | Western | 8 | HVDC | 903
2023-05-04 08:00 | Western | 11 | Solar | 46.47
2023-05-04 09:00 | Eastern | 1 | Gas | 4766
2023-05-04 09:00 | Eastern | 2 | HFO | 1163.2
2023-05-04 09:00 | Eastern | 10 | Tripura | 126
2023-05-04 09:00 | Eastern | 11 | Solar | 37
2023-05-04 09:00 | Western | 1 | Gas | 904
2023-05-04 09:00 | Western | 2 | HFO | 264
2023-05-04 09:00 | Western | 3 | HSD | 0
2023-05-04 09:00 | Western | 6 | Coal | 1935
2023-05-04 09:00 | Western | 8 | HVDC | 905
2023-05-04 09:00 | Western | 11 | Solar | 156.65
2023-05-04 10:00 | Eastern | 1 | Gas | 4573
2023-05-04 10:00 | Eastern | 2 | HFO | 1395.2
2023-05-04 10:00 | Eastern | 5 | Hydro | 25
2023-05-04 10:00 | Eastern | 10 | Tripura | 134
2023-05-04 10:00 | Eastern | 11 | Solar | 71
2023-05-04 10:00 | Western | 1 | Gas | 862
2023-05-04 10:00 | Western | 2 | HFO | 361
2023-05-04 10:00 | Western | 3 | HSD | 0
2023-05-04 10:00 | Western | 6 | Coal | 1929
2023-05-04 10:00 | Western | 8 | HVDC | 904
2023-05-04 10:00 | Western | 11 | Solar | 262.88
2023-05-04 11:00 | Eastern | 1 | Gas | 4605
2023-05-04 11:00 | Eastern | 2 | HFO | 1644.2
2023-05-04 11:00 | Eastern | 5 | Hydro | 25
2023-05-04 11:00 | Eastern | 10 | Tripura | 138
2023-05-04 11:00 | Eastern | 11 | Solar | 111
2023-05-04 11:00 | Western | 1 | Gas | 850
2023-05-04 11:00 | Western | 2 | HFO | 374
2023-05-04 11:00 | Western | 3 | HSD | 0
2023-05-04 11:00 | Western | 6 | Coal | 1887
2023-05-04 11:00 | Western | 8 | HVDC | 903
2023-05-04 11:00 | Western | 11 | Solar | 239.19
2023-05-04 12:00 | Eastern | 1 | Gas | 4674
2023-05-04 12:00 | Eastern | 2 | HFO | 1891.2
2023-05-04 12:00 | Eastern | 3 | HSD | 211
2023-05-04 12:00 | Eastern | 5 | Hydro | 25
2023-05-04 12:00 | Eastern | 10 | Tripura | 148
2023-05-04 12:00 | Eastern | 11 | Solar | 61
2023-05-04 12:00 | Western | 1 | Gas | 844
2023-05-04 12:00 | Western | 2 | HFO | 516
2023-05-04 12:00 | Western | 3 | HSD | 0
2023-05-04 12:00 | Western | 6 | Coal | 2029
2023-05-04 12:00 | Western | 8 | HVDC | 905
2023-05-04 12:00 | Western | 11 | Solar | 70.65
2023-05-04 13:00 | Eastern | 1 | Gas | 4653
2023-05-04 13:00 | Eastern | 2 | HFO | 2169.2
2023-05-04 13:00 | Eastern | 5 | Hydro | 25
2023-05-04 13:00 | Eastern | 10 | Tripura | 154
2023-05-04 13:00 | Eastern | 11 | Solar | 88
2023-05-04 13:00 | Western | 1 | Gas | 845
2023-05-04 13:00 | Western | 2 | HFO | 652
2023-05-04 13:00 | Western | 3 | HSD | 0
2023-05-04 13:00 | Western | 6 | Coal | 2194
2023-05-04 13:00 | Western | 8 | HVDC | 905
2023-05-04 13:00 | Western | 11 | Solar | 105.4
2023-05-04 14:00 | Eastern | 1 | Gas | 4357
2023-05-04 14:00 | Eastern | 2 | HFO | 2221
2023-05-04 14:00 | Eastern | 5 | Hydro | 25
2023-05-04 14:00 | Eastern | 10 | Tripura | 156
2023-05-04 14:00 | Eastern | 11 | Solar | 80
2023-05-04 14:00 | Western | 1 | Gas | 811
2023-05-04 14:00 | Western | 2 | HFO | 674
2023-05-04 14:00 | Western | 3 | HSD | 21
2023-05-04 14:00 | Western | 6 | Coal | 2234
2023-05-04 14:00 | Western | 8 | HVDC | 904
2023-05-04 14:00 | Western | 11 | Solar | 71.96
2023-05-04 15:00 | Eastern | 1 | Gas | 4439
2023-05-04 15:00 | Eastern | 2 | HFO | 2221
2023-05-04 15:00 | Eastern | 5 | Hydro | 25
2023-05-04 15:00 | Eastern | 10 | Tripura | 158
2023-05-04 15:00 | Eastern | 11 | Solar | 68
2023-05-04 15:00 | Western | 1 | Gas | 794
2023-05-04 15:00 | Western | 2 | HFO | 512
2023-05-04 15:00 | Western | 3 | HSD | 22
2023-05-04 15:00 | Western | 6 | Coal | 2136
2023-05-04 15:00 | Western | 8 | HVDC | 905
2023-05-04 15:00 | Western | 11 | Solar | 184.38
2023-05-04 16:00 | Eastern | 1 | Gas | 4721
2023-05-04 16:00 | Eastern | 2 | HFO | 1946
2023-05-04 16:00 | Eastern | 5 | Hydro | 25
2023-05-04 16:00 | Eastern | 10 | Tripura | 152
2023-05-04 16:00 | Eastern | 11 | Solar | 53
2023-05-04 16:00 | Western | 1 | Gas | 797
2023-05-04 16:00 | Western | 2 | HFO | 446
2023-05-04 16:00 | Western | 3 | HSD | 30
2023-05-04 16:00 | Western | 6 | Coal | 2091
2023-05-04 16:00 | Western | 8 | HVDC | 904
2023-05-04 16:00 | Western | 11 | Solar | 86.29
2023-05-04 17:00 | Eastern | 1 | Gas | 4804
2023-05-04 17:00 | Eastern | 2 | HFO | 1450
2023-05-04 17:00 | Eastern | 5 | Hydro | 25
2023-05-04 17:00 | Eastern | 10 | Tripura | 146
2023-05-04 17:00 | Eastern | 11 | Solar | 17
2023-05-04 17:00 | Western | 1 | Gas | 792
2023-05-04 17:00 | Western | 2 | HFO | 437
2023-05-04 17:00 | Western | 3 | HSD | 25
2023-05-04 17:00 | Western | 6 | Coal | 2031
2023-05-04 17:00 | Western | 8 | HVDC | 905
2023-05-04 17:00 | Western | 11 | Solar | 62.82
2023-05-04 18:00 | Eastern | 1 | Gas | 4620
2023-05-04 18:00 | Eastern | 2 | HFO | 1555
2023-05-04 18:00 | Eastern | 5 | Hydro | 25
2023-05-04 18:00 | Eastern | 10 | Tripura | 142
2023-05-04 18:00 | Eastern | 11 | Solar | 1
2023-05-04 18:00 | Western | 1 | Gas | 782
2023-05-04 18:00 | Western | 2 | HFO | 407
2023-05-04 18:00 | Western | 3 | HSD | 20
2023-05-04 18:00 | Western | 6 | Coal | 2052
2023-05-04 18:00 | Western | 8 | HVDC | 904
2023-05-04 18:00 | Western | 11 | Solar | 14.06
2023-05-04 19:00 | Eastern | 1 | Gas | 4945
2023-05-04 19:00 | Eastern | 2 | HFO | 2488
2023-05-04 19:00 | Eastern | 5 | Hydro | 25
2023-05-04 19:00 | Eastern | 10 | Tripura | 164
2023-05-04 19:00 | Western | 1 | Gas | 824
2023-05-04 19:00 | Western | 2 | HFO | 588
2023-05-04 19:00 | Western | 3 | HSD | 13
2023-05-04 19:00 | Western | 6 | Coal | 2117
2023-05-04 19:00 | Western | 8 | HVDC | 903
2023-05-04 19:30 | Eastern | 1 | Gas | 4911
2023-05-04 19:30 | Eastern | 2 | HFO | 2743.2
2023-05-04 19:30 | Eastern | 5 | Hydro | 25
2023-05-04 19:30 | Eastern | 10 | Tripura | 160
2023-05-04 19:30 | Western | 1 | Gas | 848
2023-05-04 19:30 | Western | 2 | HFO | 520
2023-05-04 19:30 | Western | 3 | HSD | 0
2023-05-04 19:30 | Western | 6 | Coal | 2300
2023-05-04 19:30 | Western | 8 | HVDC | 904
2023-05-04 20:00 | Eastern | 1 | Gas | 4960
2023-05-04 20:00 | Eastern | 2 | HFO | 2724.2
2023-05-04 20:00 | Eastern | 5 | Hydro | 25
2023-05-04 20:00 | Eastern | 10 | Tripura | 162
2023-05-04 20:00 | Western | 1 | Gas | 850
2023-05-04 20:00 | Western | 2 | HFO | 403
2023-05-04 20:00 | Western | 3 | HSD | 0
2023-05-04 20:00 | Western | 6 | Coal | 2262
2023-05-04 20:00 | Western | 8 | HVDC | 904
2023-05-04 21:00 | Eastern | 1 | Gas | 5147
2023-05-04 21:00 | Eastern | 2 | HFO | 2366.2
2023-05-04 21:00 | Eastern | 5 | Hydro | 25
2023-05-04 21:00 | Eastern | 10 | Tripura | 158
2023-05-04 21:00 | Western | 1 | Gas | 880
2023-05-04 21:00 | Western | 2 | HFO | 398
2023-05-04 21:00 | Western | 3 | HSD | 0
2023-05-04 21:00 | Western | 6 | Coal | 2261
2023-05-04 21:00 | Western | 8 | HVDC | 904
2023-05-04 22:00 | Eastern | 1 | Gas | 5132
2023-05-04 22:00 | Eastern | 2 | HFO | 2107.2
2023-05-04 22:00 | Eastern | 5 | Hydro | 25
2023-05-04 22:00 | Eastern | 10 | Tripura | 162
2023-05-04 22:00 | Western | 1 | Gas | 891
2023-05-04 22:00 | Western | 2 | HFO | 398
2023-05-04 22:00 | Western | 3 | HSD | 0
2023-05-04 22:00 | Western | 6 | Coal | 2088
2023-05-04 22:00 | Western | 8 | HVDC | 904
2023-05-04 23:00 | Eastern | 1 | Gas | 5083
2023-05-04 23:00 | Eastern | 2 | HFO | 2045.2
2023-05-04 23:00 | Eastern | 5 | Hydro | 0
2023-05-04 23:00 | Eastern | 10 | Tripura | 162
2023-05-04 23:00 | Western | 1 | Gas | 906
2023-05-04 23:00 | Western | 2 | HFO | 416
2023-05-04 23:00 | Western | 3 | HSD | 0
2023-05-04 23:00 | Western | 6 | Coal | 2213
2023-05-04 23:00 | Western | 8 | HVDC | 904
2023-05-05 | Eastern | 1 | Gas | 5270
2023-05-05 | Eastern | 2 | HFO | 1696.2
2023-05-05 | Eastern | 10 | Tripura | 158
2023-05-05 | Eastern | 11 | Solar | 0
2023-05-05 | Western | 1 | Gas | 905
2023-05-05 | Western | 2 | HFO | 409
2023-05-05 | Western | 3 | HSD | 0
2023-05-05 | Western | 6 | Coal | 2175
2023-05-05 | Western | 8 | HVDC | 904
2023-05-05 01:00 | Eastern | 1 | Gas | 5003
2023-05-05 01:00 | Eastern | 2 | HFO | 1446.2
2023-05-05 01:00 | Eastern | 10 | Tripura | 158
2023-05-05 01:00 | Western | 1 | Gas | 902
2023-05-05 01:00 | Western | 2 | HFO | 400
2023-05-05 01:00 | Western | 3 | HSD | 0
2023-05-05 01:00 | Western | 6 | Coal | 2214
2023-05-05 01:00 | Western | 8 | HVDC | 905
2023-05-05 02:00 | Eastern | 1 | Gas | 4911
2023-05-05 02:00 | Eastern | 2 | HFO | 1387.2
2023-05-05 02:00 | Eastern | 10 | Tripura | 152
2023-05-05 02:00 | Western | 1 | Gas | 913
2023-05-05 02:00 | Western | 2 | HFO | 239
2023-05-05 02:00 | Western | 3 | HSD | 0
2023-05-05 02:00 | Western | 6 | Coal | 2234
2023-05-05 02:00 | Western | 8 | HVDC | 905
2023-05-05 03:00 | Eastern | 1 | Gas | 4933
2023-05-05 03:00 | Eastern | 2 | HFO | 1160.2
2023-05-05 03:00 | Eastern | 10 | Tripura | 148
2023-05-05 03:00 | Western | 1 | Gas | 915
2023-05-05 03:00 | Western | 2 | HFO | 44
2023-05-05 03:00 | Western | 3 | HSD | 0
2023-05-05 03:00 | Western | 6 | Coal | 2228
2023-05-05 03:00 | Western | 8 | HVDC | 906
2023-05-05 04:00 | Eastern | 1 | Gas | 4956
2023-05-05 04:00 | Eastern | 2 | HFO | 1008.2
2023-05-05 04:00 | Eastern | 10 | Tripura | 150
2023-05-05 04:00 | Western | 1 | Gas | 919
2023-05-05 04:00 | Western | 3 | HSD | 0
2023-05-05 04:00 | Western | 6 | Coal | 2193
2023-05-05 04:00 | Western | 8 | HVDC | 906
2023-05-05 05:00 | Eastern | 1 | Gas | 4933
2023-05-05 05:00 | Eastern | 2 | HFO | 913.2
2023-05-05 05:00 | Eastern | 10 | Tripura | 144
2023-05-05 05:00 | Western | 1 | Gas | 926
2023-05-05 05:00 | Western | 3 | HSD | 0
2023-05-05 05:00 | Western | 6 | Coal | 2094
2023-05-05 05:00 | Western | 8 | HVDC | 905
2023-05-05 06:00 | Eastern | 1 | Gas | 4670
2023-05-05 06:00 | Eastern | 2 | HFO | 724
2023-05-05 06:00 | Eastern | 10 | Tripura | 134
2023-05-05 06:00 | Eastern | 11 | Solar | 4
2023-05-05 06:00 | Western | 1 | Gas | 923
2023-05-05 06:00 | Western | 3 | HSD | 0
2023-05-05 06:00 | Western | 6 | Coal | 1982
2023-05-05 06:00 | Western | 8 | HVDC | 906
2023-05-05 06:00 | Western | 11 | Solar | 9.22
2023-05-05 07:00 | Eastern | 1 | Gas | 4803
2023-05-05 07:00 | Eastern | 2 | HFO | 706
2023-05-05 07:00 | Eastern | 10 | Tripura | 130
2023-05-05 07:00 | Eastern | 11 | Solar | 19
2023-05-05 07:00 | Western | 1 | Gas | 922
2023-05-05 07:00 | Western | 3 | HSD | 0
2023-05-05 07:00 | Western | 6 | Coal | 1987
2023-05-05 07:00 | Western | 8 | HVDC | 905
2023-05-05 07:00 | Western | 11 | Solar | 39.73
2023-05-05 08:00 | Eastern | 1 | Gas | 4741
2023-05-05 08:00 | Eastern | 2 | HFO | 766
2023-05-05 08:00 | Eastern | 10 | Tripura | 128
2023-05-05 08:00 | Eastern | 11 | Solar | 44
2023-05-05 08:00 | Western | 1 | Gas | 915
2023-05-05 08:00 | Western | 2 | HFO | 0
2023-05-05 08:00 | Western | 3 | HSD | 0
2023-05-05 08:00 | Western | 6 | Coal | 2079
2023-05-05 08:00 | Western | 8 | HVDC | 906
2023-05-05 08:00 | Western | 11 | Solar | 104.38
2023-05-05 09:00 | Eastern | 1 | Gas | 4683
2023-05-05 09:00 | Eastern | 2 | HFO | 833
2023-05-05 09:00 | Eastern | 10 | Tripura | 126
2023-05-05 09:00 | Eastern | 11 | Solar | 77
2023-05-05 09:00 | Western | 1 | Gas | 890
2023-05-05 09:00 | Western | 2 | HFO | 3
2023-05-05 09:00 | Western | 3 | HSD | 0
2023-05-05 09:00 | Western | 6 | Coal | 1911
2023-05-05 09:00 | Western | 8 | HVDC | 905
2023-05-05 09:00 | Western | 11 | Solar | 167.6
2023-05-05 10:00 | Eastern | 1 | Gas | 4746
2023-05-05 10:00 | Eastern | 2 | HFO | 943
2023-05-05 10:00 | Eastern | 5 | Hydro | 0
2023-05-05 10:00 | Eastern | 10 | Tripura | 126
2023-05-05 10:00 | Eastern | 11 | Solar | 46
2023-05-05 10:00 | Western | 1 | Gas | 862
2023-05-05 10:00 | Western | 2 | HFO | 35
2023-05-05 10:00 | Western | 3 | HSD | 25
2023-05-05 10:00 | Western | 6 | Coal | 1889
2023-05-05 10:00 | Western | 8 | HVDC | 905
2023-05-05 10:00 | Western | 11 | Solar | 284.1
2023-05-05 11:00 | Eastern | 1 | Gas | 4672
2023-05-05 11:00 | Eastern | 2 | HFO | 1149
2023-05-05 11:00 | Eastern | 5 | Hydro | 25
2023-05-05 11:00 | Eastern | 10 | Tripura | 136
2023-05-05 11:00 | Eastern | 11 | Solar | 66
2023-05-05 11:00 | Western | 1 | Gas | 833
2023-05-05 11:00 | Western | 2 | HFO | 35
2023-05-05 11:00 | Western | 3 | HSD | 47
2023-05-05 11:00 | Western | 6 | Coal | 1986
2023-05-05 11:00 | Western | 8 | HVDC | 905
2023-05-05 11:00 | Western | 11 | Solar | 342.81
2023-05-05 12:00 | Eastern | 1 | Gas | 4728
2023-05-05 12:00 | Eastern | 2 | HFO | 1234
2023-05-05 12:00 | Eastern | 5 | Hydro | 25
2023-05-05 12:00 | Eastern | 10 | Tripura | 146
2023-05-05 12:00 | Eastern | 11 | Solar | 90
2023-05-05 12:00 | Western | 1 | Gas | 844
2023-05-05 12:00 | Western | 2 | HFO | 148
2023-05-05 12:00 | Western | 3 | HSD | 162
2023-05-05 12:00 | Western | 6 | Coal | 2100.59
2023-05-05 12:00 | Western | 8 | HVDC | 905
2023-05-05 12:00 | Western | 11 | Solar | 293.91
2023-05-05 13:00 | Eastern | 1 | Gas | 4751
2023-05-05 13:00 | Eastern | 2 | HFO | 1467
2023-05-05 13:00 | Eastern | 5 | Hydro | 25
2023-05-05 13:00 | Eastern | 10 | Tripura | 154
2023-05-05 13:00 | Eastern | 11 | Solar | 95
2023-05-05 13:00 | Western | 1 | Gas | 846
2023-05-05 13:00 | Western | 2 | HFO | 225
2023-05-05 13:00 | Western | 3 | HSD | 225
2023-05-05 13:00 | Western | 6 | Coal | 2145
2023-05-05 13:00 | Western | 8 | HVDC | 903
2023-05-05 13:00 | Western | 11 | Solar | 288.2
2023-05-05 14:00 | Eastern | 1 | Gas | 4908
2023-05-05 14:00 | Eastern | 2 | HFO | 1129
2023-05-05 14:00 | Eastern | 5 | Hydro | 25
2023-05-05 14:00 | Eastern | 10 | Tripura | 144
2023-05-05 14:00 | Eastern | 11 | Solar | 92
2023-05-05 14:00 | Western | 1 | Gas | 825
2023-05-05 14:00 | Western | 2 | HFO | 119
2023-05-05 14:00 | Western | 3 | HSD | 254
2023-05-05 14:00 | Western | 6 | Coal | 2077
2023-05-05 14:00 | Western | 8 | HVDC | 904
2023-05-05 14:00 | Western | 11 | Solar | 161.29
2023-05-05 15:00 | Eastern | 1 | Gas | 5116
2023-05-05 15:00 | Eastern | 2 | HFO | 1276
2023-05-05 15:00 | Eastern | 5 | Hydro | 25
2023-05-05 15:00 | Eastern | 10 | Tripura | 154
2023-05-05 15:00 | Eastern | 11 | Solar | 70
2023-05-05 15:00 | Western | 1 | Gas | 880
2023-05-05 15:00 | Western | 2 | HFO | 93
2023-05-05 15:00 | Western | 3 | HSD | 340
2023-05-05 15:00 | Western | 6 | Coal | 2143
2023-05-05 15:00 | Western | 8 | HVDC | 904
2023-05-05 15:00 | Western | 11 | Solar | 221.27
2023-05-05 16:00 | Eastern | 1 | Gas | 4985
2023-05-05 16:00 | Eastern | 2 | HFO | 1258
2023-05-05 16:00 | Eastern | 5 | Hydro | 25
2023-05-05 16:00 | Eastern | 10 | Tripura | 146
2023-05-05 16:00 | Eastern | 11 | Solar | 50
2023-05-05 16:00 | Western | 1 | Gas | 891
2023-05-05 16:00 | Western | 3 | HSD | 347
2023-05-05 16:00 | Western | 6 | Coal | 2057
2023-05-05 16:00 | Western | 8 | HVDC | 903
2023-05-05 16:00 | Western | 11 | Solar | 97.23
2023-05-05 17:00 | Eastern | 1 | Gas | 4780
2023-05-05 17:00 | Eastern | 2 | HFO | 1006
2023-05-05 17:00 | Eastern | 5 | Hydro | 25
2023-05-05 17:00 | Eastern | 10 | Tripura | 140
2023-05-05 17:00 | Eastern | 11 | Solar | 18
2023-05-05 17:00 | Western | 1 | Gas | 907
2023-05-05 17:00 | Western | 3 | HSD | 352
2023-05-05 17:00 | Western | 6 | Coal | 1991
2023-05-05 17:00 | Western | 8 | HVDC | 904
2023-05-05 17:00 | Western | 11 | Solar | 75.15
2023-05-05 18:00 | Eastern | 1 | Gas | 4596
2023-05-05 18:00 | Eastern | 2 | HFO | 1126
2023-05-05 18:00 | Eastern | 5 | Hydro | 25
2023-05-05 18:00 | Eastern | 10 | Tripura | 128
2023-05-05 18:00 | Eastern | 11 | Solar | 3
2023-05-05 18:00 | Western | 1 | Gas | 867
2023-05-05 18:00 | Western | 2 | HFO | 9
2023-05-05 18:00 | Western | 3 | HSD | 356
2023-05-05 18:00 | Western | 6 | Coal | 1899
2023-05-05 18:00 | Western | 8 | HVDC | 903
2023-05-05 18:00 | Western | 11 | Solar | 14.19
2023-05-05 19:00 | Eastern | 1 | Gas | 5129
2023-05-05 19:00 | Eastern | 2 | HFO | 2110
2023-05-05 19:00 | Eastern | 5 | Hydro | 25
2023-05-05 19:00 | Eastern | 10 | Tripura | 154
2023-05-05 19:00 | Western | 1 | Gas | 900
2023-05-05 19:00 | Western | 2 | HFO | 226
2023-05-05 19:00 | Western | 3 | HSD | 350
2023-05-05 19:00 | Western | 6 | Coal | 2080
2023-05-05 19:00 | Western | 8 | HVDC | 904
2023-05-05 19:30 | Eastern | 1 | Gas | 5215
2023-05-05 19:30 | Eastern | 2 | HFO | 2503.2
2023-05-05 19:30 | Eastern | 5 | Hydro | 25
2023-05-05 19:30 | Eastern | 10 | Tripura | 148
2023-05-05 19:30 | Western | 1 | Gas | 948
2023-05-05 19:30 | Western | 2 | HFO | 351
2023-05-05 19:30 | Western | 3 | HSD | 315
2023-05-05 19:30 | Western | 6 | Coal | 2292
2023-05-05 19:30 | Western | 8 | HVDC | 904
2023-05-05 20:00 | Eastern | 1 | Gas | 5290
2023-05-05 20:00 | Eastern | 2 | HFO | 2481.2
2023-05-05 20:00 | Eastern | 5 | Hydro | 25
2023-05-05 20:00 | Eastern | 10 | Tripura | 152
2023-05-05 20:00 | Western | 1 | Gas | 943
2023-05-05 20:00 | Western | 2 | HFO | 355
2023-05-05 20:00 | Western | 3 | HSD | 312
2023-05-05 20:00 | Western | 6 | Coal | 2271
2023-05-05 20:00 | Western | 8 | HVDC | 904
2023-05-05 21:00 | Eastern | 1 | Gas | 5343
2023-05-05 21:00 | Eastern | 2 | HFO | 2743.2
2023-05-05 21:00 | Eastern | 5 | Hydro | 25
2023-05-05 21:00 | Eastern | 10 | Tripura | 152
2023-05-05 21:00 | Western | 1 | Gas | 953
2023-05-05 21:00 | Western | 2 | HFO | 664
2023-05-05 21:00 | Western | 3 | HSD | 20
2023-05-05 21:00 | Western | 6 | Coal | 2131
2023-05-05 21:00 | Western | 8 | HVDC | 907
2023-05-05 22:00 | Eastern | 1 | Gas | 5101
2023-05-05 22:00 | Eastern | 2 | HFO | 2933.2
2023-05-05 22:00 | Eastern | 5 | Hydro | 25
2023-05-05 22:00 | Eastern | 10 | Tripura | 158
2023-05-05 22:00 | Western | 1 | Gas | 965
2023-05-05 22:00 | Western | 2 | HFO | 827
2023-05-05 22:00 | Western | 3 | HSD | 0
2023-05-05 22:00 | Western | 6 | Coal | 1967
2023-05-05 22:00 | Western | 8 | HVDC | 907
2023-05-05 23:00 | Eastern | 1 | Gas | 5196
2023-05-05 23:00 | Eastern | 2 | HFO | 2608.2
2023-05-05 23:00 | Eastern | 5 | Hydro | 0
2023-05-05 23:00 | Eastern | 10 | Tripura | 158
2023-05-05 23:00 | Western | 1 | Gas | 957
2023-05-05 23:00 | Western | 2 | HFO | 831
2023-05-05 23:00 | Western | 3 | HSD | 0
2023-05-05 23:00 | Western | 6 | Coal | 2085
2023-05-05 23:00 | Western | 8 | HVDC | 910
2023-05-06 | Eastern | 1 | Gas | 5285
2023-05-06 | Eastern | 2 | HFO | 2022.2
2023-05-06 | Eastern | 3 | HSD | 0
2023-05-06 | Eastern | 5 | Hydro | 0
2023-05-06 | Eastern | 10 | Tripura | 154
2023-05-06 | Western | 1 | Gas | 944
2023-05-06 | Western | 2 | HFO | 829
2023-05-06 | Western | 3 | HSD | 0
2023-05-06 | Western | 6 | Coal | 2205
2023-05-06 | Western | 8 | HVDC | 904
2023-05-06 01:00 | Eastern | 1 | Gas | 5281
2023-05-06 01:00 | Eastern | 2 | HFO | 1585.2
2023-05-06 01:00 | Eastern | 10 | Tripura | 150
2023-05-06 01:00 | Western | 1 | Gas | 945
2023-05-06 01:00 | Western | 2 | HFO | 726
2023-05-06 01:00 | Western | 6 | Coal | 2319
2023-05-06 01:00 | Western | 8 | HVDC | 904
2023-05-06 02:00 | Eastern | 1 | Gas | 5226
2023-05-06 02:00 | Eastern | 2 | HFO | 1550.2
2023-05-06 02:00 | Eastern | 10 | Tripura | 146
2023-05-06 02:00 | Western | 1 | Gas | 955
2023-05-06 02:00 | Western | 2 | HFO | 341
2023-05-06 02:00 | Western | 6 | Coal | 2272
2023-05-06 02:00 | Western | 8 | HVDC | 904
2023-05-06 03:00 | Eastern | 1 | Gas | 5273
2023-05-06 03:00 | Eastern | 2 | HFO | 1430.2
2023-05-06 03:00 | Eastern | 10 | Tripura | 142
2023-05-06 03:00 | Western | 1 | Gas | 958
2023-05-06 03:00 | Western | 2 | HFO | 172
2023-05-06 03:00 | Western | 6 | Coal | 2048
2023-05-06 03:00 | Western | 8 | HVDC | 906
2023-05-06 04:00 | Eastern | 1 | Gas | 5248
2023-05-06 04:00 | Eastern | 2 | HFO | 1293.2
2023-05-06 04:00 | Eastern | 10 | Tripura | 138
2023-05-06 04:00 | Western | 1 | Gas | 962
2023-05-06 04:00 | Western | 2 | HFO | 137
2023-05-06 04:00 | Western | 6 | Coal | 2027
2023-05-06 04:00 | Western | 8 | HVDC | 907
2023-05-06 05:00 | Eastern | 1 | Gas | 5213
2023-05-06 05:00 | Eastern | 2 | HFO | 1012.2
2023-05-06 05:00 | Eastern | 10 | Tripura | 134
2023-05-06 05:00 | Western | 1 | Gas | 967
2023-05-06 05:00 | Western | 2 | HFO | 68
2023-05-06 05:00 | Western | 6 | Coal | 2161
2023-05-06 05:00 | Western | 8 | HVDC | 906
2023-05-06 06:00 | Eastern | 1 | Gas | 5161
2023-05-06 06:00 | Eastern | 2 | HFO | 737.2
2023-05-06 06:00 | Eastern | 10 | Tripura | 124
2023-05-06 06:00 | Eastern | 11 | Solar | 4
2023-05-06 06:00 | Western | 1 | Gas | 933
2023-05-06 06:00 | Western | 2 | HFO | 32
2023-05-06 06:00 | Western | 6 | Coal | 2132
2023-05-06 06:00 | Western | 8 | HVDC | 907
2023-05-06 06:00 | Western | 11 | Solar | 13.22
2023-05-06 07:00 | Eastern | 1 | Gas | 5133
2023-05-06 07:00 | Eastern | 2 | HFO | 766.2
2023-05-06 07:00 | Eastern | 10 | Tripura | 122
2023-05-06 07:00 | Eastern | 11 | Solar | 18
2023-05-06 07:00 | Western | 1 | Gas | 945
2023-05-06 07:00 | Western | 2 | HFO | 32
2023-05-06 07:00 | Western | 6 | Coal | 2091
2023-05-06 07:00 | Western | 8 | HVDC | 907
2023-05-06 07:00 | Western | 11 | Solar | 78.85
2023-05-06 08:00 | Eastern | 1 | Gas | 5281
2023-05-06 08:00 | Eastern | 2 | HFO | 715
2023-05-06 08:00 | Eastern | 10 | Tripura | 130
2023-05-06 08:00 | Eastern | 11 | Solar | 49
2023-05-06 08:00 | Western | 1 | Gas | 914
2023-05-06 08:00 | Western | 2 | HFO | 32
2023-05-06 08:00 | Western | 6 | Coal | 2092
2023-05-06 08:00 | Western | 8 | HVDC | 911
2023-05-06 08:00 | Western | 11 | Solar | 168.06
2023-05-06 09:00 | Eastern | 1 | Gas | 5239
2023-05-06 09:00 | Eastern | 2 | HFO | 959
2023-05-06 09:00 | Eastern | 10 | Tripura | 146
2023-05-06 09:00 | Eastern | 11 | Solar | 73
2023-05-06 09:00 | Western | 1 | Gas | 937
2023-05-06 09:00 | Western | 2 | HFO | 144
2023-05-06 09:00 | Western | 6 | Coal | 2214
2023-05-06 09:00 | Western | 8 | HVDC | 911
2023-05-06 09:00 | Western | 11 | Solar | 215.84
2023-05-06 10:00 | Eastern | 1 | Gas | 5209
2023-05-06 10:00 | Eastern | 2 | HFO | 1258
2023-05-06 10:00 | Eastern | 10 | Tripura | 156
2023-05-06 10:00 | Eastern | 11 | Solar | 77
2023-05-06 10:00 | Western | 1 | Gas | 890
2023-05-06 10:00 | Western | 2 | HFO | 171
2023-05-06 10:00 | Western | 6 | Coal | 2255
2023-05-06 10:00 | Western | 8 | HVDC | 911
2023-05-06 10:00 | Western | 11 | Solar | 310.36
2023-05-06 11:00 | Eastern | 1 | Gas | 5259
2023-05-06 11:00 | Eastern | 2 | HFO | 1651
2023-05-06 11:00 | Eastern | 5 | Hydro | 25
2023-05-06 11:00 | Eastern | 10 | Tripura | 160
2023-05-06 11:00 | Eastern | 11 | Solar | 72
2023-05-06 11:00 | Western | 1 | Gas | 867
2023-05-06 11:00 | Western | 2 | HFO | 211
2023-05-06 11:00 | Western | 3 | HSD | 20
2023-05-06 11:00 | Western | 6 | Coal | 2197
2023-05-06 11:00 | Western | 8 | HVDC | 911
2023-05-06 11:00 | Western | 11 | Solar | 340.03
2023-05-06 12:00 | Eastern | 1 | Gas | 5189
2023-05-06 12:00 | Eastern | 2 | HFO | 1772
2023-05-06 12:00 | Eastern | 5 | Hydro | 25
2023-05-06 12:00 | Eastern | 10 | Tripura | 160
2023-05-06 12:00 | Eastern | 11 | Solar | 91
2023-05-06 12:00 | Western | 1 | Gas | 853
2023-05-06 12:00 | Western | 2 | HFO | 416
2023-05-06 12:00 | Western | 3 | HSD | 20
2023-05-06 12:00 | Western | 6 | Coal | 2274
2023-05-06 12:00 | Western | 8 | HVDC | 911
2023-05-06 12:00 | Western | 11 | Solar | 336.24
2023-05-06 13:00 | Eastern | 1 | Gas | 5064
2023-05-06 13:00 | Eastern | 2 | HFO | 1921
2023-05-06 13:00 | Eastern | 5 | Hydro | 25
2023-05-06 13:00 | Eastern | 10 | Tripura | 174
2023-05-06 13:00 | Eastern | 11 | Solar | 100
2023-05-06 13:00 | Western | 1 | Gas | 837
2023-05-06 13:00 | Western | 2 | HFO | 624
2023-05-06 13:00 | Western | 3 | HSD | 20
2023-05-06 13:00 | Western | 6 | Coal | 2315
2023-05-06 13:00 | Western | 8 | HVDC | 912
2023-05-06 13:00 | Western | 11 | Solar | 350.18
2023-05-06 14:00 | Eastern | 1 | Gas | 4972
2023-05-06 14:00 | Eastern | 2 | HFO | 1961
2023-05-06 14:00 | Eastern | 5 | Hydro | 25
2023-05-06 14:00 | Eastern | 10 | Tripura | 172
2023-05-06 14:00 | Eastern | 11 | Solar | 96
2023-05-06 14:00 | Western | 1 | Gas | 803
2023-05-06 14:00 | Western | 2 | HFO | 728
2023-05-06 14:00 | Western | 3 | HSD | 0
2023-05-06 14:00 | Western | 6 | Coal | 2300
2023-05-06 14:00 | Western | 8 | HVDC | 911
2023-05-06 14:00 | Western | 11 | Solar | 309.64
2023-05-06 15:00 | Eastern | 1 | Gas | 5017
2023-05-06 15:00 | Eastern | 2 | HFO | 2013
2023-05-06 15:00 | Eastern | 5 | Hydro | 25
2023-05-06 15:00 | Eastern | 10 | Tripura | 162
2023-05-06 15:00 | Eastern | 11 | Solar | 74
2023-05-06 15:00 | Western | 1 | Gas | 807
2023-05-06 15:00 | Western | 2 | HFO | 836
2023-05-06 15:00 | Western | 6 | Coal | 2314
2023-05-06 15:00 | Western | 8 | HVDC | 911
2023-05-06 15:00 | Western | 11 | Solar | 233.53
2023-05-06 16:00 | Eastern | 1 | Gas | 4842
2023-05-06 16:00 | Eastern | 2 | HFO | 1800
2023-05-06 16:00 | Eastern | 5 | Hydro | 25
2023-05-06 16:00 | Eastern | 10 | Tripura | 160
2023-05-06 16:00 | Eastern | 11 | Solar | 48
2023-05-06 16:00 | Western | 1 | Gas | 772
2023-05-06 16:00 | Western | 2 | HFO | 798
2023-05-06 16:00 | Western | 6 | Coal | 2340
2023-05-06 16:00 | Western | 8 | HVDC | 908
2023-05-06 16:00 | Western | 11 | Solar | 159
2023-05-06 17:00 | Eastern | 1 | Gas | 4997
2023-05-06 17:00 | Eastern | 2 | HFO | 1899
2023-05-06 17:00 | Eastern | 5 | Hydro | 25
2023-05-06 17:00 | Eastern | 10 | Tripura | 138
2023-05-06 17:00 | Eastern | 11 | Solar | 21
2023-05-06 17:00 | Western | 1 | Gas | 774
2023-05-06 17:00 | Western | 2 | HFO | 548
2023-05-06 17:00 | Western | 6 | Coal | 2330.67
2023-05-06 17:00 | Western | 8 | HVDC | 905
2023-05-06 17:00 | Western | 11 | Solar | 84.02
2023-05-06 18:00 | Eastern | 1 | Gas | 4919
2023-05-06 18:00 | Eastern | 2 | HFO | 2120
2023-05-06 18:00 | Eastern | 5 | Hydro | 25
2023-05-06 18:00 | Eastern | 10 | Tripura | 140
2023-05-06 18:00 | Eastern | 11 | Solar | 3
2023-05-06 18:00 | Western | 1 | Gas | 787
2023-05-06 18:00 | Western | 2 | HFO | 553
2023-05-06 18:00 | Western | 6 | Coal | 2123.48
2023-05-06 18:00 | Western | 8 | HVDC | 906
2023-05-06 18:00 | Western | 11 | Solar | 14.19
2023-05-06 19:00 | Eastern | 1 | Gas | 5190
2023-05-06 19:00 | Eastern | 2 | HFO | 2803
2023-05-06 19:00 | Eastern | 3 | HSD | 0
2023-05-06 19:00 | Eastern | 5 | Hydro | 25
2023-05-06 19:00 | Eastern | 10 | Tripura | 164
2023-05-06 19:00 | Eastern | 11 | Solar | 0
2023-05-06 19:00 | Western | 1 | Gas | 801
2023-05-06 19:00 | Western | 2 | HFO | 1086
2023-05-06 19:00 | Western | 6 | Coal | 2192.79
2023-05-06 19:00 | Western | 8 | HVDC | 906
2023-05-06 19:00 | Western | 11 | Solar | 0
2023-05-06 19:30 | Eastern | 1 | Gas | 5336
2023-05-06 19:30 | Eastern | 2 | HFO | 3093
2023-05-06 19:30 | Eastern | 3 | HSD | 280
2023-05-06 19:30 | Eastern | 5 | Hydro | 25
2023-05-06 19:30 | Eastern | 10 | Tripura | 158
2023-05-06 19:30 | Western | 1 | Gas | 822
2023-05-06 19:30 | Western | 2 | HFO | 1232
2023-05-06 19:30 | Western | 6 | Coal | 2320.57
2023-05-06 19:30 | Western | 8 | HVDC | 810
2023-05-06 20:00 | Eastern | 1 | Gas | 5236
2023-05-06 20:00 | Eastern | 2 | HFO | 3210
2023-05-06 20:00 | Eastern | 3 | HSD | 240
2023-05-06 20:00 | Eastern | 5 | Hydro | 25
2023-05-06 20:00 | Eastern | 10 | Tripura | 152
2023-05-06 20:00 | Western | 1 | Gas | 837
2023-05-06 20:00 | Western | 2 | HFO | 1262
2023-05-06 20:00 | Western | 6 | Coal | 2287.78
2023-05-06 20:00 | Western | 8 | HVDC | 801
2023-05-06 21:00 | Eastern | 1 | Gas | 5265
2023-05-06 21:00 | Eastern | 2 | HFO | 3172
2023-05-06 21:00 | Eastern | 3 | HSD | 180
2023-05-06 21:00 | Eastern | 5 | Hydro | 25
2023-05-06 21:00 | Eastern | 10 | Tripura | 152
2023-05-06 21:00 | Western | 1 | Gas | 848
2023-05-06 21:00 | Western | 2 | HFO | 1326
2023-05-06 21:00 | Western | 6 | Coal | 2327
2023-05-06 21:00 | Western | 8 | HVDC | 802
2023-05-06 22:00 | Eastern | 1 | Gas | 5262
2023-05-06 22:00 | Eastern | 2 | HFO | 3043
2023-05-06 22:00 | Eastern | 5 | Hydro | 25
2023-05-06 22:00 | Eastern | 10 | Tripura | 154
2023-05-06 22:00 | Western | 1 | Gas | 850
2023-05-06 22:00 | Western | 2 | HFO | 1310
2023-05-06 22:00 | Western | 6 | Coal | 2339
2023-05-06 22:00 | Western | 8 | HVDC | 840
2023-05-06 23:00 | Eastern | 1 | Gas | 5382
2023-05-06 23:00 | Eastern | 2 | HFO | 2585.2
2023-05-06 23:00 | Eastern | 5 | Hydro | 0
2023-05-06 23:00 | Eastern | 10 | Tripura | 158
2023-05-06 23:00 | Western | 1 | Gas | 851
2023-05-06 23:00 | Western | 2 | HFO | 1210
2023-05-06 23:00 | Western | 6 | Coal | 2329
2023-05-06 23:00 | Western | 8 | HVDC | 841
2023-05-07 | Eastern | 1 | Gas | 5310
2023-05-07 | Eastern | 2 | HFO | 1995.2
2023-05-07 | Eastern | 3 | HSD | 0
2023-05-07 | Eastern | 10 | Tripura | 166
2023-05-07 | Eastern | 11 | Solar | 0
2023-05-07 | Western | 1 | Gas | 853
2023-05-07 | Western | 2 | HFO | 1130
2023-05-07 | Western | 6 | Coal | 2331
2023-05-07 | Western | 8 | HVDC | 908
2023-05-07 01:00 | Eastern | 1 | Gas | 5232
2023-05-07 01:00 | Eastern | 2 | HFO | 1650.2
2023-05-07 01:00 | Eastern | 10 | Tripura | 162
2023-05-07 01:00 | Western | 1 | Gas | 860
2023-05-07 01:00 | Western | 2 | HFO | 989
2023-05-07 01:00 | Western | 6 | Coal | 2331
2023-05-07 01:00 | Western | 8 | HVDC | 908
2023-05-07 02:00 | Eastern | 1 | Gas | 5273
2023-05-07 02:00 | Eastern | 2 | HFO | 1610.2
2023-05-07 02:00 | Eastern | 10 | Tripura | 152
2023-05-07 02:00 | Western | 1 | Gas | 868
2023-05-07 02:00 | Western | 2 | HFO | 933
2023-05-07 02:00 | Western | 6 | Coal | 2326
2023-05-07 02:00 | Western | 8 | HVDC | 906
2023-05-07 03:00 | Eastern | 1 | Gas | 5294
2023-05-07 03:00 | Eastern | 2 | HFO | 1484.2
2023-05-07 03:00 | Eastern | 10 | Tripura | 154
2023-05-07 03:00 | Western | 1 | Gas | 880
2023-05-07 03:00 | Western | 2 | HFO | 763
2023-05-07 03:00 | Western | 6 | Coal | 2329
2023-05-07 03:00 | Western | 8 | HVDC | 909
2023-05-07 04:00 | Eastern | 1 | Gas | 5245
2023-05-07 04:00 | Eastern | 2 | HFO | 1459.2
2023-05-07 04:00 | Eastern | 10 | Tripura | 148
2023-05-07 04:00 | Western | 1 | Gas | 899
2023-05-07 04:00 | Western | 2 | HFO | 677
2023-05-07 04:00 | Western | 6 | Coal | 2331
2023-05-07 04:00 | Western | 8 | HVDC | 910
2023-05-07 05:00 | Eastern | 1 | Gas | 5253
2023-05-07 05:00 | Eastern | 2 | HFO | 1374.2
2023-05-07 05:00 | Eastern | 10 | Tripura | 144
2023-05-07 05:00 | Western | 1 | Gas | 908
2023-05-07 05:00 | Western | 2 | HFO | 477
2023-05-07 05:00 | Western | 6 | Coal | 2327
2023-05-07 05:00 | Western | 8 | HVDC | 909
2023-05-07 06:00 | Eastern | 1 | Gas | 5264
2023-05-07 06:00 | Eastern | 2 | HFO | 1053.2
2023-05-07 06:00 | Eastern | 10 | Tripura | 128
2023-05-07 06:00 | Eastern | 11 | Solar | 3
2023-05-07 06:00 | Western | 1 | Gas | 906
2023-05-07 06:00 | Western | 2 | HFO | 221
2023-05-07 06:00 | Western | 6 | Coal | 2327
2023-05-07 06:00 | Western | 8 | HVDC | 909
2023-05-07 06:00 | Western | 11 | Solar | 14.21
2023-05-07 07:00 | Eastern | 1 | Gas | 5294
2023-05-07 07:00 | Eastern | 2 | HFO | 1044.2
2023-05-07 07:00 | Eastern | 10 | Tripura | 116
2023-05-07 07:00 | Eastern | 11 | Solar | 26
2023-05-07 07:00 | Western | 1 | Gas | 896
2023-05-07 07:00 | Western | 2 | HFO | 221
2023-05-07 07:00 | Western | 6 | Coal | 2327
2023-05-07 07:00 | Western | 8 | HVDC | 910
2023-05-07 07:00 | Western | 11 | Solar | 70.98
2023-05-07 08:00 | Eastern | 1 | Gas | 5166
2023-05-07 08:00 | Eastern | 2 | HFO | 1180.2
2023-05-07 08:00 | Eastern | 10 | Tripura | 134
2023-05-07 08:00 | Eastern | 11 | Solar | 52
2023-05-07 08:00 | Western | 1 | Gas | 879
2023-05-07 08:00 | Western | 2 | HFO | 377
2023-05-07 08:00 | Western | 6 | Coal | 2336
2023-05-07 08:00 | Western | 8 | HVDC | 910
2023-05-07 08:00 | Western | 11 | Solar | 153.23
2023-05-07 09:00 | Eastern | 1 | Gas | 5253
2023-05-07 09:00 | Eastern | 2 | HFO | 1433
2023-05-07 09:00 | Eastern | 5 | Hydro | 0
2023-05-07 09:00 | Eastern | 10 | Tripura | 138
2023-05-07 09:00 | Eastern | 11 | Solar | 72
2023-05-07 09:00 | Western | 1 | Gas | 854
2023-05-07 09:00 | Western | 2 | HFO | 407
2023-05-07 09:00 | Western | 6 | Coal | 2282
2023-05-07 09:00 | Western | 8 | HVDC | 910
2023-05-07 09:00 | Western | 11 | Solar | 225.53
2023-05-07 10:00 | Eastern | 1 | Gas | 5126
2023-05-07 10:00 | Eastern | 2 | HFO | 1861
2023-05-07 10:00 | Eastern | 3 | HSD | 342
2023-05-07 10:00 | Eastern | 5 | Hydro | 25
2023-05-07 10:00 | Eastern | 10 | Tripura | 146
2023-05-07 10:00 | Eastern | 11 | Solar | 94
2023-05-07 10:00 | Western | 1 | Gas | 823
2023-05-07 10:00 | Western | 2 | HFO | 411
2023-05-07 10:00 | Western | 3 | HSD | 0
2023-05-07 10:00 | Western | 6 | Coal | 2244
2023-05-07 10:00 | Western | 8 | HVDC | 907
2023-05-07 10:00 | Western | 11 | Solar | 210.54
2023-05-07 11:00 | Eastern | 1 | Gas | 5096
2023-05-07 11:00 | Eastern | 2 | HFO | 2156
2023-05-07 11:00 | Eastern | 3 | HSD | 452
2023-05-07 11:00 | Eastern | 5 | Hydro | 25
2023-05-07 11:00 | Eastern | 10 | Tripura | 150
2023-05-07 11:00 | Eastern | 11 | Solar | 99
2023-05-07 11:00 | Western | 1 | Gas | 799
2023-05-07 11:00 | Western | 2 | HFO | 481
2023-05-07 11:00 | Western | 3 | HSD | 0
2023-05-07 11:00 | Western | 6 | Coal | 2288
2023-05-07 11:00 | Western | 8 | HVDC | 907
2023-05-07 11:00 | Western | 11 | Solar | 311.02
2023-05-07 12:00 | Eastern | 1 | Gas | 5096
2023-05-07 12:00 | Eastern | 2 | HFO | 2155
2023-05-07 12:00 | Eastern | 3 | HSD | 456
2023-05-07 12:00 | Eastern | 5 | Hydro | 25
2023-05-07 12:00 | Eastern | 10 | Tripura | 156
2023-05-07 12:00 | Eastern | 11 | Solar | 96
2023-05-07 12:00 | Western | 1 | Gas | 771
2023-05-07 12:00 | Western | 2 | HFO | 529
2023-05-07 12:00 | Western | 3 | HSD | 0
2023-05-07 12:00 | Western | 6 | Coal | 2280
2023-05-07 12:00 | Western | 8 | HVDC | 908
2023-05-07 12:00 | Western | 11 | Solar | 324.77
2023-05-07 13:00 | Eastern | 1 | Gas | 5066
2023-05-07 13:00 | Eastern | 2 | HFO | 2390
2023-05-07 13:00 | Eastern | 3 | HSD | 404
2023-05-07 13:00 | Eastern | 5 | Hydro | 25
2023-05-07 13:00 | Eastern | 10 | Tripura | 158
2023-05-07 13:00 | Eastern | 11 | Solar | 105
2023-05-07 13:00 | Western | 1 | Gas | 784
2023-05-07 13:00 | Western | 2 | HFO | 658
2023-05-07 13:00 | Western | 3 | HSD | 0
2023-05-07 13:00 | Western | 6 | Coal | 2297
2023-05-07 13:00 | Western | 8 | HVDC | 908
2023-05-07 13:00 | Western | 11 | Solar | 303.9
2023-05-07 14:00 | Eastern | 1 | Gas | 5088
2023-05-07 14:00 | Eastern | 2 | HFO | 2246
2023-05-07 14:00 | Eastern | 3 | HSD | 460
2023-05-07 14:00 | Eastern | 5 | Hydro | 25
2023-05-07 14:00 | Eastern | 10 | Tripura | 160
2023-05-07 14:00 | Eastern | 11 | Solar | 97
2023-05-07 14:00 | Western | 1 | Gas | 781
2023-05-07 14:00 | Western | 2 | HFO | 689
2023-05-07 14:00 | Western | 6 | Coal | 2297
2023-05-07 14:00 | Western | 8 | HVDC | 907
2023-05-07 14:00 | Western | 11 | Solar | 273.44
2023-05-07 15:00 | Eastern | 1 | Gas | 5112
2023-05-07 15:00 | Eastern | 2 | HFO | 1995
2023-05-07 15:00 | Eastern | 3 | HSD | 340
2023-05-07 15:00 | Eastern | 5 | Hydro | 25
2023-05-07 15:00 | Eastern | 10 | Tripura | 168
2023-05-07 15:00 | Eastern | 11 | Solar | 74
2023-05-07 15:00 | Western | 1 | Gas | 772
2023-05-07 15:00 | Western | 2 | HFO | 702
2023-05-07 15:00 | Western | 3 | HSD | 0
2023-05-07 15:00 | Western | 6 | Coal | 2285
2023-05-07 15:00 | Western | 8 | HVDC | 908
2023-05-07 15:00 | Western | 11 | Solar | 199.54
2023-05-07 16:00 | Eastern | 1 | Gas | 5129
2023-05-07 16:00 | Eastern | 2 | HFO | 2114
2023-05-07 16:00 | Eastern | 5 | Hydro | 25
2023-05-07 16:00 | Eastern | 10 | Tripura | 156
2023-05-07 16:00 | Eastern | 11 | Solar | 46
2023-05-07 16:00 | Western | 1 | Gas | 770
2023-05-07 16:00 | Western | 2 | HFO | 712
2023-05-07 16:00 | Western | 3 | HSD | 0
2023-05-07 16:00 | Western | 6 | Coal | 2304
2023-05-07 16:00 | Western | 8 | HVDC | 908
2023-05-07 16:00 | Western | 11 | Solar | 145
2023-05-07 17:00 | Eastern | 1 | Gas | 5121
2023-05-07 17:00 | Eastern | 2 | HFO | 2171
2023-05-07 17:00 | Eastern | 5 | Hydro | 25
2023-05-07 17:00 | Eastern | 10 | Tripura | 150
2023-05-07 17:00 | Eastern | 11 | Solar | 20
2023-05-07 17:00 | Western | 1 | Gas | 773
2023-05-07 17:00 | Western | 2 | HFO | 771
2023-05-07 17:00 | Western | 3 | HSD | 0
2023-05-07 17:00 | Western | 6 | Coal | 2301
2023-05-07 17:00 | Western | 8 | HVDC | 908
2023-05-07 17:00 | Western | 11 | Solar | 68.05
2023-05-07 18:00 | Eastern | 1 | Gas | 5000
2023-05-07 18:00 | Eastern | 2 | HFO | 2234
2023-05-07 18:00 | Eastern | 5 | Hydro | 25
2023-05-07 18:00 | Eastern | 10 | Tripura | 148
2023-05-07 18:00 | Eastern | 11 | Solar | 3
2023-05-07 18:00 | Western | 1 | Gas | 788
2023-05-07 18:00 | Western | 2 | HFO | 864
2023-05-07 18:00 | Western | 3 | HSD | 0
2023-05-07 18:00 | Western | 6 | Coal | 2243
2023-05-07 18:00 | Western | 8 | HVDC | 909
2023-05-07 18:00 | Western | 11 | Solar | 12.19
2023-05-07 19:00 | Eastern | 1 | Gas | 5223
2023-05-07 19:00 | Eastern | 2 | HFO | 2857
2023-05-07 19:00 | Eastern | 3 | HSD | 449
2023-05-07 19:00 | Eastern | 5 | Hydro | 25
2023-05-07 19:00 | Eastern | 10 | Tripura | 146
2023-05-07 19:00 | Western | 1 | Gas | 775
2023-05-07 19:00 | Western | 2 | HFO | 1164
2023-05-07 19:00 | Western | 3 | HSD | 0
2023-05-07 19:00 | Western | 6 | Coal | 2281
2023-05-07 19:00 | Western | 8 | HVDC | 908
2023-05-07 19:30 | Eastern | 1 | Gas | 5233
2023-05-07 19:30 | Eastern | 2 | HFO | 3024
2023-05-07 19:30 | Eastern | 3 | HSD | 361
2023-05-07 19:30 | Eastern | 5 | Hydro | 25
2023-05-07 19:30 | Eastern | 10 | Tripura | 154
2023-05-07 19:30 | Western | 1 | Gas | 834
2023-05-07 19:30 | Western | 2 | HFO | 1192
2023-05-07 19:30 | Western | 3 | HSD | 0
2023-05-07 19:30 | Western | 6 | Coal | 2327
2023-05-07 19:30 | Western | 8 | HVDC | 864
2023-05-07 20:00 | Eastern | 1 | Gas | 5254
2023-05-07 20:00 | Eastern | 2 | HFO | 3096
2023-05-07 20:00 | Eastern | 3 | HSD | 326
2023-05-07 20:00 | Eastern | 5 | Hydro | 25
2023-05-07 20:00 | Eastern | 10 | Tripura | 152
2023-05-07 20:00 | Western | 1 | Gas | 842
2023-05-07 20:00 | Western | 2 | HFO | 1229
2023-05-07 20:00 | Western | 3 | HSD | 0
2023-05-07 20:00 | Western | 6 | Coal | 2309
2023-05-07 20:00 | Western | 8 | HVDC | 865
2023-05-07 21:00 | Eastern | 1 | Gas | 5298
2023-05-07 21:00 | Eastern | 2 | HFO | 3076
2023-05-07 21:00 | Eastern | 3 | HSD | 453
2023-05-07 21:00 | Eastern | 5 | Hydro | 25
2023-05-07 21:00 | Eastern | 10 | Tripura | 148
2023-05-07 21:00 | Western | 1 | Gas | 852
2023-05-07 21:00 | Western | 2 | HFO | 1237
2023-05-07 21:00 | Western | 3 | HSD | 0
2023-05-07 21:00 | Western | 6 | Coal | 2329.76
2023-05-07 21:00 | Western | 8 | HVDC | 913
2023-05-07 22:00 | Eastern | 1 | Gas | 5322
2023-05-07 22:00 | Eastern | 2 | HFO | 2992
2023-05-07 22:00 | Eastern | 3 | HSD | 454
2023-05-07 22:00 | Eastern | 5 | Hydro | 25
2023-05-07 22:00 | Eastern | 10 | Tripura | 150
2023-05-07 22:00 | Western | 1 | Gas | 868
2023-05-07 22:00 | Western | 2 | HFO | 1182
2023-05-07 22:00 | Western | 3 | HSD | 0
2023-05-07 22:00 | Western | 6 | Coal | 2327.86
2023-05-07 22:00 | Western | 8 | HVDC | 846
2023-05-07 23:00 | Eastern | 1 | Gas | 5373
2023-05-07 23:00 | Eastern | 2 | HFO | 2525
2023-05-07 23:00 | Eastern | 3 | HSD | 451
2023-05-07 23:00 | Eastern | 5 | Hydro | 0
2023-05-07 23:00 | Eastern | 10 | Tripura | 168
2023-05-07 23:00 | Western | 1 | Gas | 859
2023-05-07 23:00 | Western | 2 | HFO | 1015
2023-05-07 23:00 | Western | 3 | HSD | 0
2023-05-07 23:00 | Western | 6 | Coal | 2311
2023-05-07 23:00 | Western | 8 | HVDC | 844
2023-05-08 | Eastern | 1 | Gas | 5323
2023-05-08 | Eastern | 2 | HFO | 2044
2023-05-08 | Eastern | 3 | HSD | 448
2023-05-08 | Eastern | 10 | Tripura | 166
2023-05-08 | Eastern | 11 | Solar | 0
2023-05-08 | Western | 1 | Gas | 865
2023-05-08 | Western | 2 | HFO | 980
2023-05-08 | Western | 3 | HSD | 0
2023-05-08 | Western | 6 | Coal | 2311.57
2023-05-08 | Western | 8 | HVDC | 846
2023-05-08 01:00 | Eastern | 1 | Gas | 5289
2023-05-08 01:00 | Eastern | 2 | HFO | 1693
2023-05-08 01:00 | Eastern | 3 | HSD | 450
2023-05-08 01:00 | Eastern | 10 | Tripura | 168
2023-05-08 01:00 | Western | 1 | Gas | 871
2023-05-08 01:00 | Western | 2 | HFO | 921
2023-05-08 01:00 | Western | 3 | HSD | 0
2023-05-08 01:00 | Western | 6 | Coal | 2308.33
2023-05-08 01:00 | Western | 8 | HVDC | 909
2023-05-08 02:00 | Eastern | 1 | Gas | 5255
2023-05-08 02:00 | Eastern | 2 | HFO | 1576
2023-05-08 02:00 | Eastern | 3 | HSD | 453
2023-05-08 02:00 | Eastern | 10 | Tripura | 164
2023-05-08 02:00 | Western | 1 | Gas | 898
2023-05-08 02:00 | Western | 2 | HFO | 921
2023-05-08 02:00 | Western | 3 | HSD | 0
2023-05-08 02:00 | Western | 6 | Coal | 2310.29
2023-05-08 02:00 | Western | 8 | HVDC | 909
2023-05-08 03:00 | Eastern | 1 | Gas | 5260
2023-05-08 03:00 | Eastern | 2 | HFO | 1412
2023-05-08 03:00 | Eastern | 3 | HSD | 449
2023-05-08 03:00 | Eastern | 10 | Tripura | 160
2023-05-08 03:00 | Western | 1 | Gas | 907
2023-05-08 03:00 | Western | 2 | HFO | 784
2023-05-08 03:00 | Western | 3 | HSD | 0
2023-05-08 03:00 | Western | 6 | Coal | 2306.34
2023-05-08 03:00 | Western | 8 | HVDC | 910
2023-05-08 04:00 | Eastern | 1 | Gas | 5232
2023-05-08 04:00 | Eastern | 2 | HFO | 1378
2023-05-08 04:00 | Eastern | 3 | HSD | 454
2023-05-08 04:00 | Eastern | 10 | Tripura | 156
2023-05-08 04:00 | Western | 1 | Gas | 917
2023-05-08 04:00 | Western | 2 | HFO | 759
2023-05-08 04:00 | Western | 3 | HSD | 0
2023-05-08 04:00 | Western | 6 | Coal | 2311.86
2023-05-08 04:00 | Western | 8 | HVDC | 909
2023-05-08 05:00 | Eastern | 1 | Gas | 5262
2023-05-08 05:00 | Eastern | 2 | HFO | 1374
2023-05-08 05:00 | Eastern | 3 | HSD | 149
2023-05-08 05:00 | Eastern | 10 | Tripura | 152
2023-05-08 05:00 | Western | 1 | Gas | 919
2023-05-08 05:00 | Western | 2 | HFO | 716
2023-05-08 05:00 | Western | 3 | HSD | 0
2023-05-08 05:00 | Western | 6 | Coal | 2320.54
2023-05-08 05:00 | Western | 8 | HVDC | 910
2023-05-08 06:00 | Eastern | 1 | Gas | 5083
2023-05-08 06:00 | Eastern | 2 | HFO | 1372
2023-05-08 06:00 | Eastern | 10 | Tripura | 148
2023-05-08 06:00 | Eastern | 11 | Solar | 6
2023-05-08 06:00 | Western | 1 | Gas | 929
2023-05-08 06:00 | Western | 2 | HFO | 681
2023-05-08 06:00 | Western | 3 | HSD | 0
2023-05-08 06:00 | Western | 6 | Coal | 2292.14
2023-05-08 06:00 | Western | 8 | HVDC | 909
2023-05-08 06:00 | Western | 11 | Solar | 14.22
2023-05-08 07:00 | Eastern | 1 | Gas | 5042
2023-05-08 07:00 | Eastern | 2 | HFO | 1342
2023-05-08 07:00 | Eastern | 10 | Tripura | 138
2023-05-08 07:00 | Eastern | 11 | Solar | 23
2023-05-08 07:00 | Western | 1 | Gas | 921
2023-05-08 07:00 | Western | 2 | HFO | 681
2023-05-08 07:00 | Western | 3 | HSD | 0
2023-05-08 07:00 | Western | 6 | Coal | 2227
2023-05-08 07:00 | Western | 8 | HVDC | 911
2023-05-08 07:00 | Western | 11 | Solar | 73.98
2023-05-08 08:00 | Eastern | 1 | Gas | 5030
2023-05-08 08:00 | Eastern | 2 | HFO | 1278
2023-05-08 08:00 | Eastern | 10 | Tripura | 146
2023-05-08 08:00 | Eastern | 11 | Solar | 52
2023-05-08 08:00 | Western | 1 | Gas | 883
2023-05-08 08:00 | Western | 2 | HFO | 678
2023-05-08 08:00 | Western | 3 | HSD | 0
2023-05-08 08:00 | Western | 6 | Coal | 2231
2023-05-08 08:00 | Western | 8 | HVDC | 911
2023-05-08 08:00 | Western | 11 | Solar | 155.26
2023-05-08 09:00 | Eastern | 1 | Gas | 5134
2023-05-08 09:00 | Eastern | 2 | HFO | 1309
2023-05-08 09:00 | Eastern | 3 | HSD | 105
2023-05-08 09:00 | Eastern | 10 | Tripura | 146
2023-05-08 09:00 | Eastern | 11 | Solar | 74
2023-05-08 09:00 | Western | 1 | Gas | 885
2023-05-08 09:00 | Western | 2 | HFO | 648
2023-05-08 09:00 | Western | 3 | HSD | 0
2023-05-08 09:00 | Western | 6 | Coal | 2143
2023-05-08 09:00 | Western | 8 | HVDC | 911
2023-05-08 09:00 | Western | 11 | Solar | 229.59
2023-05-08 10:00 | Eastern | 1 | Gas | 5240
2023-05-08 10:00 | Eastern | 2 | HFO | 1543
2023-05-08 10:00 | Eastern | 3 | HSD | 10
2023-05-08 10:00 | Eastern | 5 | Hydro | 0
2023-05-08 10:00 | Eastern | 10 | Tripura | 152
2023-05-08 10:00 | Eastern | 11 | Solar | 91
2023-05-08 10:00 | Western | 1 | Gas | 875
2023-05-08 10:00 | Western | 2 | HFO | 598
2023-05-08 10:00 | Western | 3 | HSD | 0
2023-05-08 10:00 | Western | 6 | Coal | 2024
2023-05-08 10:00 | Western | 8 | HVDC | 911
2023-05-08 10:00 | Western | 11 | Solar | 292.61
2023-05-08 11:00 | Eastern | 1 | Gas | 5151
2023-05-08 11:00 | Eastern | 2 | HFO | 1786
2023-05-08 11:00 | Eastern | 5 | Hydro | 27
2023-05-08 11:00 | Eastern | 10 | Tripura | 160
2023-05-08 11:00 | Eastern | 11 | Solar | 105
2023-05-08 11:00 | Western | 1 | Gas | 872
2023-05-08 11:00 | Western | 2 | HFO | 710
2023-05-08 11:00 | Western | 3 | HSD | 0
2023-05-08 11:00 | Western | 6 | Coal | 2035
2023-05-08 11:00 | Western | 8 | HVDC | 911
2023-05-08 11:00 | Western | 11 | Solar | 325
2023-05-08 12:00 | Eastern | 1 | Gas | 5194
2023-05-08 12:00 | Eastern | 2 | HFO | 1986
2023-05-08 12:00 | Eastern | 5 | Hydro | 27
2023-05-08 12:00 | Eastern | 10 | Tripura | 162
2023-05-08 12:00 | Eastern | 11 | Solar | 109
2023-05-08 12:00 | Western | 1 | Gas | 788
2023-05-08 12:00 | Western | 2 | HFO | 732
2023-05-08 12:00 | Western | 3 | HSD | 0
2023-05-08 12:00 | Western | 6 | Coal | 2055
2023-05-08 12:00 | Western | 8 | HVDC | 911
2023-05-08 12:00 | Western | 11 | Solar | 326.01
2023-05-08 13:00 | Eastern | 1 | Gas | 5135
2023-05-08 13:00 | Eastern | 2 | HFO | 2016
2023-05-08 13:00 | Eastern | 5 | Hydro | 27
2023-05-08 13:00 | Eastern | 10 | Tripura | 160
2023-05-08 13:00 | Eastern | 11 | Solar | 97
2023-05-08 13:00 | Western | 1 | Gas | 807
2023-05-08 13:00 | Western | 2 | HFO | 736
2023-05-08 13:00 | Western | 3 | HSD | 0
2023-05-08 13:00 | Western | 6 | Coal | 2107
2023-05-08 13:00 | Western | 8 | HVDC | 911
2023-05-08 13:00 | Western | 11 | Solar | 321.8
2023-05-08 14:00 | Eastern | 1 | Gas | 5149
2023-05-08 14:00 | Eastern | 2 | HFO | 1811
2023-05-08 14:00 | Eastern | 5 | Hydro | 27
2023-05-08 14:00 | Eastern | 10 | Tripura | 160
2023-05-08 14:00 | Eastern | 11 | Solar | 92
2023-05-08 14:00 | Western | 1 | Gas | 808
2023-05-08 14:00 | Western | 2 | HFO | 713
2023-05-08 14:00 | Western | 3 | HSD | 0
2023-05-08 14:00 | Western | 6 | Coal | 2182
2023-05-08 14:00 | Western | 8 | HVDC | 910
2023-05-08 14:00 | Western | 11 | Solar | 267.52
2023-05-08 15:00 | Eastern | 1 | Gas | 5178
2023-05-08 15:00 | Eastern | 2 | HFO | 1785
2023-05-08 15:00 | Eastern | 3 | HSD | 72
2023-05-08 15:00 | Eastern | 5 | Hydro | 27
2023-05-08 15:00 | Eastern | 10 | Tripura | 156
2023-05-08 15:00 | Eastern | 11 | Solar | 72
2023-05-08 15:00 | Western | 1 | Gas | 799
2023-05-08 15:00 | Western | 2 | HFO | 653
2023-05-08 15:00 | Western | 3 | HSD | 0
2023-05-08 15:00 | Western | 6 | Coal | 2311
2023-05-08 15:00 | Western | 8 | HVDC | 911
2023-05-08 15:00 | Western | 11 | Solar | 224.78
2023-05-08 16:00 | Eastern | 1 | Gas | 5149
2023-05-08 16:00 | Eastern | 2 | HFO | 1831
2023-05-08 16:00 | Eastern | 3 | HSD | 358
2023-05-08 16:00 | Eastern | 5 | Hydro | 27
2023-05-08 16:00 | Eastern | 10 | Tripura | 156
2023-05-08 16:00 | Eastern | 11 | Solar | 38
2023-05-08 16:00 | Western | 1 | Gas | 795
2023-05-08 16:00 | Western | 2 | HFO | 703
2023-05-08 16:00 | Western | 3 | HSD | 0
2023-05-08 16:00 | Western | 6 | Coal | 2319
2023-05-08 16:00 | Western | 8 | HVDC | 910
2023-05-08 16:00 | Western | 11 | Solar | 158.66
2023-05-08 17:00 | Eastern | 1 | Gas | 5149
2023-05-08 17:00 | Eastern | 2 | HFO | 1853.2
2023-05-08 17:00 | Eastern | 3 | HSD | 464
2023-05-08 17:00 | Eastern | 5 | Hydro | 27
2023-05-08 17:00 | Eastern | 10 | Tripura | 154
2023-05-08 17:00 | Eastern | 11 | Solar | 22
2023-05-08 17:00 | Western | 1 | Gas | 788
2023-05-08 17:00 | Western | 2 | HFO | 748
2023-05-08 17:00 | Western | 3 | HSD | 0
2023-05-08 17:00 | Western | 6 | Coal | 2319
2023-05-08 17:00 | Western | 8 | HVDC | 911
2023-05-08 17:00 | Western | 11 | Solar | 72.19
2023-05-08 18:00 | Eastern | 1 | Gas | 5190
2023-05-08 18:00 | Eastern | 2 | HFO | 2092
2023-05-08 18:00 | Eastern | 3 | HSD | 61
2023-05-08 18:00 | Eastern | 5 | Hydro | 27
2023-05-08 18:00 | Eastern | 10 | Tripura | 156
2023-05-08 18:00 | Eastern | 11 | Solar | 3
2023-05-08 18:00 | Western | 1 | Gas | 834
2023-05-08 18:00 | Western | 2 | HFO | 795
2023-05-08 18:00 | Western | 3 | HSD | 0
2023-05-08 18:00 | Western | 6 | Coal | 2265
2023-05-08 18:00 | Western | 8 | HVDC | 910
2023-05-08 18:00 | Western | 11 | Solar | 13.19
2023-05-08 19:00 | Eastern | 1 | Gas | 5198
2023-05-08 19:00 | Eastern | 2 | HFO | 2836
2023-05-08 19:00 | Eastern | 3 | HSD | 461
2023-05-08 19:00 | Eastern | 5 | Hydro | 27
2023-05-08 19:00 | Eastern | 10 | Tripura | 158
2023-05-08 19:00 | Western | 1 | Gas | 916
2023-05-08 19:00 | Western | 2 | HFO | 981
2023-05-08 19:00 | Western | 3 | HSD | 0
2023-05-08 19:00 | Western | 6 | Coal | 2219
2023-05-08 19:00 | Western | 8 | HVDC | 911
2023-05-08 19:30 | Eastern | 1 | Gas | 5201
2023-05-08 19:30 | Eastern | 2 | HFO | 2897
2023-05-08 19:30 | Eastern | 3 | HSD | 360
2023-05-08 19:30 | Eastern | 5 | Hydro | 27
2023-05-08 19:30 | Eastern | 10 | Tripura | 164
2023-05-08 19:30 | Western | 1 | Gas | 916
2023-05-08 19:30 | Western | 2 | HFO | 1129
2023-05-08 19:30 | Western | 3 | HSD | 0
2023-05-08 19:30 | Western | 6 | Coal | 2282
2023-05-08 19:30 | Western | 8 | HVDC | 816
2023-05-08 20:00 | Eastern | 1 | Gas | 5270
2023-05-08 20:00 | Eastern | 2 | HFO | 2942
2023-05-08 20:00 | Eastern | 3 | HSD | 364
2023-05-08 20:00 | Eastern | 5 | Hydro | 27
2023-05-08 20:00 | Eastern | 10 | Tripura | 160
2023-05-08 20:00 | Western | 1 | Gas | 909
2023-05-08 20:00 | Western | 2 | HFO | 1139
2023-05-08 20:00 | Western | 3 | HSD | 0
2023-05-08 20:00 | Western | 6 | Coal | 2290
2023-05-08 20:00 | Western | 8 | HVDC | 816
2023-05-08 21:00 | Eastern | 1 | Gas | 5283
2023-05-08 21:00 | Eastern | 2 | HFO | 2928
2023-05-08 21:00 | Eastern | 3 | HSD | 458
2023-05-08 21:00 | Eastern | 5 | Hydro | 27
2023-05-08 21:00 | Eastern | 10 | Tripura | 156
2023-05-08 21:00 | Western | 1 | Gas | 886
2023-05-08 21:00 | Western | 2 | HFO | 1108
2023-05-08 21:00 | Western | 3 | HSD | 0
2023-05-08 21:00 | Western | 6 | Coal | 2303
2023-05-08 21:00 | Western | 8 | HVDC | 816
2023-05-08 22:00 | Eastern | 1 | Gas | 5333
2023-05-08 22:00 | Eastern | 2 | HFO | 2780
2023-05-08 22:00 | Eastern | 3 | HSD | 403
2023-05-08 22:00 | Eastern | 5 | Hydro | 27
2023-05-08 22:00 | Eastern | 10 | Tripura | 166
2023-05-08 22:00 | Western | 1 | Gas | 900
2023-05-08 22:00 | Western | 2 | HFO | 1111
2023-05-08 22:00 | Western | 3 | HSD | 0
2023-05-08 22:00 | Western | 6 | Coal | 2326
2023-05-08 22:00 | Western | 8 | HVDC | 863
2023-05-08 23:00 | Eastern | 1 | Gas | 5407
2023-05-08 23:00 | Eastern | 2 | HFO | 2471
2023-05-08 23:00 | Eastern | 3 | HSD | 460
2023-05-08 23:00 | Eastern | 5 | Hydro | 0
2023-05-08 23:00 | Eastern | 10 | Tripura | 174
2023-05-08 23:00 | Western | 1 | Gas | 868
2023-05-08 23:00 | Western | 2 | HFO | 1066
2023-05-08 23:00 | Western | 3 | HSD | 0
2023-05-08 23:00 | Western | 6 | Coal | 2310
2023-05-08 23:00 | Western | 8 | HVDC | 863
2023-05-09 | Eastern | 1 | Gas | 5396
2023-05-09 | Eastern | 2 | HFO | 2128
2023-05-09 | Eastern | 3 | HSD | 455
2023-05-09 | Eastern | 10 | Tripura | 174
2023-05-09 | Western | 1 | Gas | 881
2023-05-09 | Western | 2 | HFO | 1024
2023-05-09 | Western | 3 | HSD | 0
2023-05-09 | Western | 6 | Coal | 2311
2023-05-09 | Western | 8 | HVDC | 863
2023-05-09 01:00 | Eastern | 1 | Gas | 5364
2023-05-09 01:00 | Eastern | 2 | HFO | 1753
2023-05-09 01:00 | Eastern | 3 | HSD | 412
2023-05-09 01:00 | Eastern | 10 | Tripura | 172
2023-05-09 01:00 | Western | 1 | Gas | 878
2023-05-09 01:00 | Western | 2 | HFO | 967
2023-05-09 01:00 | Western | 3 | HSD | 0
2023-05-09 01:00 | Western | 6 | Coal | 2309
2023-05-09 01:00 | Western | 8 | HVDC | 910
2023-05-09 02:00 | Eastern | 1 | Gas | 5363
2023-05-09 02:00 | Eastern | 2 | HFO | 1546
2023-05-09 02:00 | Eastern | 3 | HSD | 375
2023-05-09 02:00 | Eastern | 10 | Tripura | 168
2023-05-09 02:00 | Western | 1 | Gas | 871
2023-05-09 02:00 | Western | 2 | HFO | 929
2023-05-09 02:00 | Western | 3 | HSD | 0
2023-05-09 02:00 | Western | 6 | Coal | 2293
2023-05-09 02:00 | Western | 8 | HVDC | 909
2023-05-09 03:00 | Eastern | 1 | Gas | 5412
2023-05-09 03:00 | Eastern | 2 | HFO | 1407
2023-05-09 03:00 | Eastern | 3 | HSD | 355
2023-05-09 03:00 | Eastern | 10 | Tripura | 166
2023-05-09 03:00 | Western | 1 | Gas | 897
2023-05-09 03:00 | Western | 2 | HFO | 653
2023-05-09 03:00 | Western | 3 | HSD | 0
2023-05-09 03:00 | Western | 6 | Coal | 2311
2023-05-09 03:00 | Western | 8 | HVDC | 910
2023-05-09 04:00 | Eastern | 1 | Gas | 5375
2023-05-09 04:00 | Eastern | 2 | HFO | 1376
2023-05-09 04:00 | Eastern | 3 | HSD | 354
2023-05-09 04:00 | Eastern | 10 | Tripura | 160
2023-05-09 04:00 | Western | 1 | Gas | 897
2023-05-09 04:00 | Western | 2 | HFO | 709
2023-05-09 04:00 | Western | 3 | HSD | 0
2023-05-09 04:00 | Western | 6 | Coal | 2310
2023-05-09 04:00 | Western | 8 | HVDC | 909
2023-05-09 05:00 | Eastern | 1 | Gas | 5400
2023-05-09 05:00 | Eastern | 2 | HFO | 1372
2023-05-09 05:00 | Eastern | 3 | HSD | 225
2023-05-09 05:00 | Eastern | 10 | Tripura | 160
2023-05-09 05:00 | Western | 1 | Gas | 896
2023-05-09 05:00 | Western | 2 | HFO | 695
2023-05-09 05:00 | Western | 3 | HSD | 0
2023-05-09 05:00 | Western | 6 | Coal | 2309
2023-05-09 05:00 | Western | 8 | HVDC | 910
2023-05-09 06:00 | Eastern | 1 | Gas | 5406
2023-05-09 06:00 | Eastern | 2 | HFO | 1383
2023-05-09 06:00 | Eastern | 10 | Tripura | 144
2023-05-09 06:00 | Eastern | 11 | Solar | 6
2023-05-09 06:00 | Western | 1 | Gas | 897
2023-05-09 06:00 | Western | 2 | HFO | 700
2023-05-09 06:00 | Western | 3 | HSD | 0
2023-05-09 06:00 | Western | 6 | Coal | 2299
2023-05-09 06:00 | Western | 8 | HVDC | 910
2023-05-09 06:00 | Western | 11 | Solar | 16.24
2023-05-09 07:00 | Eastern | 1 | Gas | 5316
2023-05-09 07:00 | Eastern | 2 | HFO | 1380
2023-05-09 07:00 | Eastern | 10 | Tripura | 146
2023-05-09 07:00 | Eastern | 11 | Solar | 25
2023-05-09 07:00 | Western | 1 | Gas | 887
2023-05-09 07:00 | Western | 2 | HFO | 714
2023-05-09 07:00 | Western | 3 | HSD | 0
2023-05-09 07:00 | Western | 6 | Coal | 2292
2023-05-09 07:00 | Western | 8 | HVDC | 912
2023-05-09 07:00 | Western | 11 | Solar | 79.91
2023-05-09 08:00 | Eastern | 1 | Gas | 5288
2023-05-09 08:00 | Eastern | 2 | HFO | 1405
2023-05-09 08:00 | Eastern | 10 | Tripura | 142
2023-05-09 08:00 | Eastern | 11 | Solar | 44
2023-05-09 08:00 | Western | 1 | Gas | 858
2023-05-09 08:00 | Western | 2 | HFO | 703
2023-05-09 08:00 | Western | 3 | HSD | 0
2023-05-09 08:00 | Western | 6 | Coal | 2271
2023-05-09 08:00 | Western | 8 | HVDC | 911
2023-05-09 08:00 | Western | 11 | Solar | 154.19
2023-05-09 09:00 | Eastern | 1 | Gas | 5270
2023-05-09 09:00 | Eastern | 2 | HFO | 1419
2023-05-09 09:00 | Eastern | 10 | Tripura | 146
2023-05-09 09:00 | Eastern | 11 | Solar | 65
2023-05-09 09:00 | Western | 1 | Gas | 826
2023-05-09 09:00 | Western | 2 | HFO | 705
2023-05-09 09:00 | Western | 3 | HSD | 75
2023-05-09 09:00 | Western | 6 | Coal | 2231
2023-05-09 09:00 | Western | 8 | HVDC | 911
2023-05-09 09:00 | Western | 11 | Solar | 238.53
2023-05-09 10:00 | Eastern | 1 | Gas | 5163
2023-05-09 10:00 | Eastern | 2 | HFO | 1808
2023-05-09 10:00 | Eastern | 3 | HSD | 316
2023-05-09 10:00 | Eastern | 5 | Hydro | 0
2023-05-09 10:00 | Eastern | 10 | Tripura | 156
2023-05-09 10:00 | Eastern | 11 | Solar | 87
2023-05-09 10:00 | Western | 1 | Gas | 811
2023-05-09 10:00 | Western | 2 | HFO | 723
2023-05-09 10:00 | Western | 3 | HSD | 200
2023-05-09 10:00 | Western | 6 | Coal | 2158
2023-05-09 10:00 | Western | 8 | HVDC | 913
2023-05-09 10:00 | Western | 11 | Solar | 293.16
2023-05-09 11:00 | Eastern | 1 | Gas | 5088
2023-05-09 11:00 | Eastern | 2 | HFO | 2167
2023-05-09 11:00 | Eastern | 3 | HSD | 453
2023-05-09 11:00 | Eastern | 5 | Hydro | 27
2023-05-09 11:00 | Eastern | 10 | Tripura | 160
2023-05-09 11:00 | Eastern | 11 | Solar | 98
2023-05-09 11:00 | Western | 1 | Gas | 703
2023-05-09 11:00 | Western | 2 | HFO | 631
2023-05-09 11:00 | Western | 3 | HSD | 228
2023-05-09 11:00 | Western | 6 | Coal | 2142
2023-05-09 11:00 | Western | 8 | HVDC | 912
2023-05-09 11:00 | Western | 11 | Solar | 308.74
2023-05-09 12:00 | Eastern | 1 | Gas | 5034
2023-05-09 12:00 | Eastern | 2 | HFO | 2160
2023-05-09 12:00 | Eastern | 3 | HSD | 454
2023-05-09 12:00 | Eastern | 5 | Hydro | 27
2023-05-09 12:00 | Eastern | 10 | Tripura | 160
2023-05-09 12:00 | Eastern | 11 | Solar | 102
2023-05-09 12:00 | Western | 1 | Gas | 731
2023-05-09 12:00 | Western | 2 | HFO | 657
2023-05-09 12:00 | Western | 3 | HSD | 200
2023-05-09 12:00 | Western | 6 | Coal | 2217
2023-05-09 12:00 | Western | 8 | HVDC | 911
2023-05-09 12:00 | Western | 11 | Solar | 317.19
2023-05-09 13:00 | Eastern | 1 | Gas | 5114
2023-05-09 13:00 | Eastern | 2 | HFO | 2167
2023-05-09 13:00 | Eastern | 3 | HSD | 204
2023-05-09 13:00 | Eastern | 5 | Hydro | 27
2023-05-09 13:00 | Eastern | 10 | Tripura | 156
2023-05-09 13:00 | Eastern | 11 | Solar | 94
2023-05-09 13:00 | Western | 1 | Gas | 774
2023-05-09 13:00 | Western | 2 | HFO | 757
2023-05-09 13:00 | Western | 3 | HSD | 120
2023-05-09 13:00 | Western | 6 | Coal | 2285
2023-05-09 13:00 | Western | 8 | HVDC | 911
2023-05-09 13:00 | Western | 11 | Solar | 318.96
2023-05-09 14:00 | Eastern | 1 | Gas | 5002
2023-05-09 14:00 | Eastern | 2 | HFO | 1881
2023-05-09 14:00 | Eastern | 3 | HSD | 229
2023-05-09 14:00 | Eastern | 5 | Hydro | 27
2023-05-09 14:00 | Eastern | 10 | Tripura | 160
2023-05-09 14:00 | Eastern | 11 | Solar | 66
2023-05-09 14:00 | Western | 1 | Gas | 782
2023-05-09 14:00 | Western | 2 | HFO | 713
2023-05-09 14:00 | Western | 3 | HSD | 40
2023-05-09 14:00 | Western | 6 | Coal | 2316
2023-05-09 14:00 | Western | 8 | HVDC | 908
2023-05-09 14:00 | Western | 11 | Solar | 296.45
2023-05-09 15:00 | Eastern | 1 | Gas | 5071
2023-05-09 15:00 | Eastern | 2 | HFO | 1814
2023-05-09 15:00 | Eastern | 3 | HSD | 445
2023-05-09 15:00 | Eastern | 5 | Hydro | 27
2023-05-09 15:00 | Eastern | 10 | Tripura | 162
2023-05-09 15:00 | Eastern | 11 | Solar | 67
2023-05-09 15:00 | Western | 1 | Gas | 799
2023-05-09 15:00 | Western | 2 | HFO | 731
2023-05-09 15:00 | Western | 3 | HSD | 0
2023-05-09 15:00 | Western | 6 | Coal | 2300
2023-05-09 15:00 | Western | 8 | HVDC | 908
2023-05-09 15:00 | Western | 11 | Solar | 230.65
2023-05-09 16:00 | Eastern | 1 | Gas | 5078
2023-05-09 16:00 | Eastern | 2 | HFO | 1830
2023-05-09 16:00 | Eastern | 3 | HSD | 274
2023-05-09 16:00 | Eastern | 5 | Hydro | 27
2023-05-09 16:00 | Eastern | 10 | Tripura | 158
2023-05-09 16:00 | Eastern | 11 | Solar | 46
2023-05-09 16:00 | Western | 1 | Gas | 822
2023-05-09 16:00 | Western | 2 | HFO | 717
2023-05-09 16:00 | Western | 3 | HSD | 0
2023-05-09 16:00 | Western | 6 | Coal | 2287
2023-05-09 16:00 | Western | 8 | HVDC | 908
2023-05-09 16:00 | Western | 11 | Solar | 152.41
2023-05-09 17:00 | Eastern | 1 | Gas | 5106
2023-05-09 17:00 | Eastern | 2 | HFO | 1851
2023-05-09 17:00 | Eastern | 3 | HSD | 237
2023-05-09 17:00 | Eastern | 5 | Hydro | 27
2023-05-09 17:00 | Eastern | 10 | Tripura | 152
2023-05-09 17:00 | Eastern | 11 | Solar | 21
2023-05-09 17:00 | Western | 1 | Gas | 837
2023-05-09 17:00 | Western | 2 | HFO | 716
2023-05-09 17:00 | Western | 3 | HSD | 0
2023-05-09 17:00 | Western | 6 | Coal | 2312
2023-05-09 17:00 | Western | 8 | HVDC | 909
2023-05-09 17:00 | Western | 11 | Solar | 68.11
2023-05-09 18:00 | Eastern | 1 | Gas | 5161
2023-05-09 18:00 | Eastern | 2 | HFO | 2056
2023-05-09 18:00 | Eastern | 3 | HSD | 61
2023-05-09 18:00 | Eastern | 5 | Hydro | 27
2023-05-09 18:00 | Eastern | 10 | Tripura | 154
2023-05-09 18:00 | Eastern | 11 | Solar | 3
2023-05-09 18:00 | Western | 1 | Gas | 850
2023-05-09 18:00 | Western | 2 | HFO | 947
2023-05-09 18:00 | Western | 3 | HSD | 0
2023-05-09 18:00 | Western | 6 | Coal | 2321
2023-05-09 18:00 | Western | 8 | HVDC | 909
2023-05-09 18:00 | Western | 11 | Solar | 12.2
2023-05-09 19:00 | Eastern | 1 | Gas | 5107
2023-05-09 19:00 | Eastern | 2 | HFO | 2820
2023-05-09 19:00 | Eastern | 3 | HSD | 442
2023-05-09 19:00 | Eastern | 5 | Hydro | 27
2023-05-09 19:00 | Eastern | 10 | Tripura | 156
2023-05-09 19:00 | Western | 1 | Gas | 853
2023-05-09 19:00 | Western | 2 | HFO | 1070
2023-05-09 19:00 | Western | 3 | HSD | 0
2023-05-09 19:00 | Western | 6 | Coal | 2203
2023-05-09 19:00 | Western | 8 | HVDC | 909
2023-05-09 19:30 | Eastern | 1 | Gas | 5169
2023-05-09 19:30 | Eastern | 2 | HFO | 2909
2023-05-09 19:30 | Eastern | 3 | HSD | 280
2023-05-09 19:30 | Eastern | 5 | Hydro | 27
2023-05-09 19:30 | Eastern | 10 | Tripura | 152
2023-05-09 19:30 | Western | 1 | Gas | 885
2023-05-09 19:30 | Western | 2 | HFO | 1101
2023-05-09 19:30 | Western | 3 | HSD | 0
2023-05-09 19:30 | Western | 6 | Coal | 2213
2023-05-09 19:30 | Western | 8 | HVDC | 908
2023-05-09 20:00 | Eastern | 1 | Gas | 5214
2023-05-09 20:00 | Eastern | 2 | HFO | 2946
2023-05-09 20:00 | Eastern | 3 | HSD | 236
2023-05-09 20:00 | Eastern | 5 | Hydro | 27
2023-05-09 20:00 | Eastern | 10 | Tripura | 152
2023-05-09 20:00 | Western | 1 | Gas | 908
2023-05-09 20:00 | Western | 2 | HFO | 1103
2023-05-09 20:00 | Western | 3 | HSD | 0
2023-05-09 20:00 | Western | 6 | Coal | 2209
2023-05-09 20:00 | Western | 8 | HVDC | 814
2023-05-09 21:00 | Eastern | 1 | Gas | 5313
2023-05-09 21:00 | Eastern | 2 | HFO | 2801
2023-05-09 21:00 | Eastern | 3 | HSD | 462
2023-05-09 21:00 | Eastern | 5 | Hydro | 27
2023-05-09 21:00 | Eastern | 10 | Tripura | 154
2023-05-09 21:00 | Western | 1 | Gas | 917
2023-05-09 21:00 | Western | 2 | HFO | 1103
2023-05-09 21:00 | Western | 3 | HSD | 0
2023-05-09 21:00 | Western | 6 | Coal | 2161
2023-05-09 21:00 | Western | 8 | HVDC | 814
2023-05-09 22:00 | Eastern | 1 | Gas | 5379
2023-05-09 22:00 | Eastern | 2 | HFO | 2818
2023-05-09 22:00 | Eastern | 3 | HSD | 463
2023-05-09 22:00 | Eastern | 5 | Hydro | 27
2023-05-09 22:00 | Eastern | 10 | Tripura | 164
2023-05-09 22:00 | Western | 1 | Gas | 934
2023-05-09 22:00 | Western | 2 | HFO | 1102
2023-05-09 22:00 | Western | 3 | HSD | 0
2023-05-09 22:00 | Western | 6 | Coal | 2208
2023-05-09 22:00 | Western | 8 | HVDC | 813
2023-05-09 23:00 | Eastern | 1 | Gas | 5132
2023-05-09 23:00 | Eastern | 2 | HFO | 2695
2023-05-09 23:00 | Eastern | 3 | HSD | 110
2023-05-09 23:00 | Eastern | 5 | Hydro | 0
2023-05-09 23:00 | Eastern | 10 | Tripura | 176
2023-05-09 23:00 | Western | 1 | Gas | 881
2023-05-09 23:00 | Western | 2 | HFO | 1060
2023-05-09 23:00 | Western | 3 | HSD | 0
2023-05-09 23:00 | Western | 6 | Coal | 2169
2023-05-09 23:00 | Western | 8 | HVDC | 771
2023-05-10 | Eastern | 1 | Gas | 5324
2023-05-10 | Eastern | 2 | HFO | 2467
2023-05-10 | Eastern | 3 | HSD | 62
2023-05-10 | Eastern | 10 | Tripura | 170
2023-05-10 | Eastern | 11 | Solar | 0
2023-05-10 | Western | 1 | Gas | 935
2023-05-10 | Western | 2 | HFO | 1043
2023-05-10 | Western | 3 | HSD | 0
2023-05-10 | Western | 6 | Coal | 2110
2023-05-10 | Western | 8 | HVDC | 813
2023-05-10 | Western | 11 | Solar | 0
2023-05-10 01:00 | Eastern | 1 | Gas | 5417
2023-05-10 01:00 | Eastern | 2 | HFO | 1929
2023-05-10 01:00 | Eastern | 3 | HSD | 445
2023-05-10 01:00 | Eastern | 10 | Tripura | 162
2023-05-10 01:00 | Western | 1 | Gas | 945
2023-05-10 01:00 | Western | 2 | HFO | 943
2023-05-10 01:00 | Western | 3 | HSD | 0
2023-05-10 01:00 | Western | 6 | Coal | 2178
2023-05-10 01:00 | Western | 8 | HVDC | 828
2023-05-10 02:00 | Eastern | 1 | Gas | 5469.5
2023-05-10 02:00 | Eastern | 2 | HFO | 1449
2023-05-10 02:00 | Eastern | 3 | HSD | 452
2023-05-10 02:00 | Eastern | 10 | Tripura | 162
2023-05-10 02:00 | Western | 1 | Gas | 950
2023-05-10 02:00 | Western | 2 | HFO | 912
2023-05-10 02:00 | Western | 3 | HSD | 0
2023-05-10 02:00 | Western | 6 | Coal | 2189
2023-05-10 02:00 | Western | 8 | HVDC | 830
2023-05-10 03:00 | Eastern | 1 | Gas | 5451
2023-05-10 03:00 | Eastern | 2 | HFO | 1367
2023-05-10 03:00 | Eastern | 3 | HSD | 457
2023-05-10 03:00 | Eastern | 10 | Tripura | 164
2023-05-10 03:00 | Western | 1 | Gas | 958
2023-05-10 03:00 | Western | 2 | HFO | 728
2023-05-10 03:00 | Western | 3 | HSD | 0
2023-05-10 03:00 | Western | 6 | Coal | 2212
2023-05-10 03:00 | Western | 8 | HVDC | 911
2023-05-10 04:00 | Eastern | 1 | Gas | 5430
2023-05-10 04:00 | Eastern | 2 | HFO | 1336
2023-05-10 04:00 | Eastern | 3 | HSD | 369
2023-05-10 04:00 | Eastern | 10 | Tripura | 158
2023-05-10 04:00 | Western | 1 | Gas | 955
2023-05-10 04:00 | Western | 2 | HFO | 711
2023-05-10 04:00 | Western | 3 | HSD | 0
2023-05-10 04:00 | Western | 6 | Coal | 2265
2023-05-10 04:00 | Western | 8 | HVDC | 914
2023-05-10 05:00 | Eastern | 1 | Gas | 5440
2023-05-10 05:00 | Eastern | 2 | HFO | 1348
2023-05-10 05:00 | Eastern | 3 | HSD | 361
2023-05-10 05:00 | Eastern | 10 | Tripura | 152
2023-05-10 05:00 | Western | 1 | Gas | 967
2023-05-10 05:00 | Western | 2 | HFO | 657
2023-05-10 05:00 | Western | 3 | HSD | 0
2023-05-10 05:00 | Western | 6 | Coal | 2302
2023-05-10 05:00 | Western | 8 | HVDC | 914
2023-05-10 06:00 | Eastern | 1 | Gas | 5282
2023-05-10 06:00 | Eastern | 2 | HFO | 1293.8
2023-05-10 06:00 | Eastern | 3 | HSD | 100
2023-05-10 06:00 | Eastern | 10 | Tripura | 146
2023-05-10 06:00 | Eastern | 11 | Solar | 5
2023-05-10 06:00 | Western | 1 | Gas | 963
2023-05-10 06:00 | Western | 2 | HFO | 657
2023-05-10 06:00 | Western | 3 | HSD | 0
2023-05-10 06:00 | Western | 6 | Coal | 2308
2023-05-10 06:00 | Western | 8 | HVDC | 914
2023-05-10 06:00 | Western | 11 | Solar | 16.24
2023-05-10 07:00 | Eastern | 1 | Gas | 5171
2023-05-10 07:00 | Eastern | 2 | HFO | 1294
2023-05-10 07:00 | Eastern | 10 | Tripura | 140
2023-05-10 07:00 | Eastern | 11 | Solar | 22
2023-05-10 07:00 | Western | 1 | Gas | 853
2023-05-10 07:00 | Western | 2 | HFO | 702
2023-05-10 07:00 | Western | 3 | HSD | 0
2023-05-10 07:00 | Western | 6 | Coal | 2224
2023-05-10 07:00 | Western | 8 | HVDC | 916
2023-05-10 07:00 | Western | 11 | Solar | 70.97
2023-05-10 08:00 | Eastern | 1 | Gas | 5170
2023-05-10 08:00 | Eastern | 2 | HFO | 1306
2023-05-10 08:00 | Eastern | 10 | Tripura | 150
2023-05-10 08:00 | Eastern | 11 | Solar | 50
2023-05-10 08:00 | Western | 1 | Gas | 851
2023-05-10 08:00 | Western | 2 | HFO | 742
2023-05-10 08:00 | Western | 3 | HSD | 0
2023-05-10 08:00 | Western | 6 | Coal | 2232
2023-05-10 08:00 | Western | 8 | HVDC | 917
2023-05-10 08:00 | Western | 11 | Solar | 158.12
2023-05-10 09:00 | Eastern | 1 | Gas | 5169
2023-05-10 09:00 | Eastern | 2 | HFO | 1359
2023-05-10 09:00 | Eastern | 3 | HSD | 0
2023-05-10 09:00 | Eastern | 10 | Tripura | 148
2023-05-10 09:00 | Eastern | 11 | Solar | 74
2023-05-10 09:00 | Western | 1 | Gas | 847
2023-05-10 09:00 | Western | 2 | HFO | 788
2023-05-10 09:00 | Western | 3 | HSD | 0
2023-05-10 09:00 | Western | 6 | Coal | 2210
2023-05-10 09:00 | Western | 8 | HVDC | 916
2023-05-10 09:00 | Western | 11 | Solar | 233.38
2023-05-10 10:00 | Eastern | 1 | Gas | 5244
2023-05-10 10:00 | Eastern | 2 | HFO | 1808
2023-05-10 10:00 | Eastern | 3 | HSD | 78
2023-05-10 10:00 | Eastern | 5 | Hydro | 0
2023-05-10 10:00 | Eastern | 10 | Tripura | 150
2023-05-10 10:00 | Eastern | 11 | Solar | 90
2023-05-10 10:00 | Western | 1 | Gas | 890
2023-05-10 10:00 | Western | 2 | HFO | 782
2023-05-10 10:00 | Western | 3 | HSD | 0
2023-05-10 10:00 | Western | 6 | Coal | 2205
2023-05-10 10:00 | Western | 8 | HVDC | 916
2023-05-10 10:00 | Western | 11 | Solar | 289.23
2023-05-10 11:00 | Eastern | 1 | Gas | 5305
2023-05-10 11:00 | Eastern | 2 | HFO | 1939
2023-05-10 11:00 | Eastern | 3 | HSD | 402
2023-05-10 11:00 | Eastern | 5 | Hydro | 25
2023-05-10 11:00 | Eastern | 10 | Tripura | 160
2023-05-10 11:00 | Eastern | 11 | Solar | 101
2023-05-10 11:00 | Western | 1 | Gas | 881
2023-05-10 11:00 | Western | 2 | HFO | 767
2023-05-10 11:00 | Western | 3 | HSD | 50
2023-05-10 11:00 | Western | 6 | Coal | 2258
2023-05-10 11:00 | Western | 8 | HVDC | 917
2023-05-10 11:00 | Western | 11 | Solar | 311.88
2023-05-10 12:00 | Eastern | 1 | Gas | 5252
2023-05-10 12:00 | Eastern | 2 | HFO | 1954
2023-05-10 12:00 | Eastern | 3 | HSD | 440
2023-05-10 12:00 | Eastern | 5 | Hydro | 25
2023-05-10 12:00 | Eastern | 10 | Tripura | 160
2023-05-10 12:00 | Eastern | 11 | Solar | 103
2023-05-10 12:00 | Western | 1 | Gas | 891
2023-05-10 12:00 | Western | 2 | HFO | 849
2023-05-10 12:00 | Western | 3 | HSD | 222
2023-05-10 12:00 | Western | 6 | Coal | 2254
2023-05-10 12:00 | Western | 8 | HVDC | 917
2023-05-10 12:00 | Western | 11 | Solar | 315.05
2023-05-10 13:00 | Eastern | 1 | Gas | 5232
2023-05-10 13:00 | Eastern | 2 | HFO | 1959
2023-05-10 13:00 | Eastern | 3 | HSD | 446
2023-05-10 13:00 | Eastern | 5 | Hydro | 25
2023-05-10 13:00 | Eastern | 10 | Tripura | 156
2023-05-10 13:00 | Eastern | 11 | Solar | 96
2023-05-10 13:00 | Western | 1 | Gas | 862
2023-05-10 13:00 | Western | 2 | HFO | 849
2023-05-10 13:00 | Western | 3 | HSD | 226
2023-05-10 13:00 | Western | 6 | Coal | 2240
2023-05-10 13:00 | Western | 8 | HVDC | 917
2023-05-10 13:00 | Western | 11 | Solar | 315.91
2023-05-10 14:00 | Eastern | 1 | Gas | 5180
2023-05-10 14:00 | Eastern | 2 | HFO | 1743
2023-05-10 14:00 | Eastern | 3 | HSD | 364
2023-05-10 14:00 | Eastern | 5 | Hydro | 25
2023-05-10 14:00 | Eastern | 10 | Tripura | 156
2023-05-10 14:00 | Eastern | 11 | Solar | 70
2023-05-10 14:00 | Western | 1 | Gas | 870
2023-05-10 14:00 | Western | 2 | HFO | 748
2023-05-10 14:00 | Western | 3 | HSD | 223
2023-05-10 14:00 | Western | 6 | Coal | 2334
2023-05-10 14:00 | Western | 8 | HVDC | 916
2023-05-10 14:00 | Western | 11 | Solar | 298.28
2023-05-10 15:00 | Eastern | 1 | Gas | 5162
2023-05-10 15:00 | Eastern | 2 | HFO | 1737
2023-05-10 15:00 | Eastern | 3 | HSD | 441
2023-05-10 15:00 | Eastern | 5 | Hydro | 25
2023-05-10 15:00 | Eastern | 10 | Tripura | 166
2023-05-10 15:00 | Eastern | 11 | Solar | 70
2023-05-10 15:00 | Western | 1 | Gas | 875
2023-05-10 15:00 | Western | 2 | HFO | 707
2023-05-10 15:00 | Western | 3 | HSD | 175
2023-05-10 15:00 | Western | 6 | Coal | 2321
2023-05-10 15:00 | Western | 8 | HVDC | 917
2023-05-10 15:00 | Western | 11 | Solar | 236.42
2023-05-10 16:00 | Eastern | 1 | Gas | 5109
2023-05-10 16:00 | Eastern | 2 | HFO | 1747
2023-05-10 16:00 | Eastern | 3 | HSD | 275
2023-05-10 16:00 | Eastern | 5 | Hydro | 25
2023-05-10 16:00 | Eastern | 10 | Tripura | 162
2023-05-10 16:00 | Eastern | 11 | Solar | 13
2023-05-10 16:00 | Western | 1 | Gas | 875
2023-05-10 16:00 | Western | 2 | HFO | 683
2023-05-10 16:00 | Western | 3 | HSD | 175
2023-05-10 16:00 | Western | 6 | Coal | 2317
2023-05-10 16:00 | Western | 8 | HVDC | 916
2023-05-10 16:00 | Western | 11 | Solar | 156
2023-05-10 17:00 | Eastern | 1 | Gas | 5115
2023-05-10 17:00 | Eastern | 2 | HFO | 1718
2023-05-10 17:00 | Eastern | 3 | HSD | 189
2023-05-10 17:00 | Eastern | 5 | Hydro | 25
2023-05-10 17:00 | Eastern | 10 | Tripura | 160
2023-05-10 17:00 | Eastern | 11 | Solar | 16
2023-05-10 17:00 | Western | 1 | Gas | 881
2023-05-10 17:00 | Western | 2 | HFO | 689
2023-05-10 17:00 | Western | 3 | HSD | 120
2023-05-10 17:00 | Western | 6 | Coal | 2306
2023-05-10 17:00 | Western | 8 | HVDC | 917
2023-05-10 17:00 | Western | 11 | Solar | 74.92
2023-05-10 18:00 | Eastern | 1 | Gas | 4900
2023-05-10 18:00 | Eastern | 2 | HFO | 2006
2023-05-10 18:00 | Eastern | 3 | HSD | 11
2023-05-10 18:00 | Eastern | 5 | Hydro | 25
2023-05-10 18:00 | Eastern | 10 | Tripura | 162
2023-05-10 18:00 | Eastern | 11 | Solar | 2
2023-05-10 18:00 | Western | 1 | Gas | 800
2023-05-10 18:00 | Western | 2 | HFO | 655
2023-05-10 18:00 | Western | 3 | HSD | 120
2023-05-10 18:00 | Western | 6 | Coal | 2185
2023-05-10 18:00 | Western | 8 | HVDC | 916
2023-05-10 18:00 | Western | 11 | Solar | 11.2
2023-05-10 19:00 | Eastern | 1 | Gas | 5224
2023-05-10 19:00 | Eastern | 2 | HFO | 2825
2023-05-10 19:00 | Eastern | 3 | HSD | 324
2023-05-10 19:00 | Eastern | 5 | Hydro | 25
2023-05-10 19:00 | Eastern | 10 | Tripura | 170
2023-05-10 19:00 | Western | 1 | Gas | 840
2023-05-10 19:00 | Western | 2 | HFO | 800
2023-05-10 19:00 | Western | 3 | HSD | 60
2023-05-10 19:00 | Western | 6 | Coal | 2146
2023-05-10 19:00 | Western | 8 | HVDC | 917
2023-05-10 19:30 | Eastern | 1 | Gas | 5291.5
2023-05-10 19:30 | Eastern | 2 | HFO | 3033
2023-05-10 19:30 | Eastern | 3 | HSD | 260
2023-05-10 19:30 | Eastern | 5 | Hydro | 25
2023-05-10 19:30 | Eastern | 10 | Tripura | 162
2023-05-10 19:30 | Western | 1 | Gas | 834
2023-05-10 19:30 | Western | 2 | HFO | 951
2023-05-10 19:30 | Western | 3 | HSD | 230
2023-05-10 19:30 | Western | 6 | Coal | 2288
2023-05-10 19:30 | Western | 8 | HVDC | 888
2023-05-10 20:00 | Eastern | 1 | Gas | 5299.5
2023-05-10 20:00 | Eastern | 2 | HFO | 2946
2023-05-10 20:00 | Eastern | 3 | HSD | 86
2023-05-10 20:00 | Eastern | 5 | Hydro | 25
2023-05-10 20:00 | Eastern | 10 | Tripura | 168
2023-05-10 20:00 | Western | 1 | Gas | 940
2023-05-10 20:00 | Western | 2 | HFO | 967
2023-05-10 20:00 | Western | 3 | HSD | 230
2023-05-10 20:00 | Western | 6 | Coal | 2308
2023-05-10 20:00 | Western | 8 | HVDC | 814
2023-05-10 21:00 | Eastern | 1 | Gas | 5333.5
2023-05-10 21:00 | Eastern | 2 | HFO | 2851
2023-05-10 21:00 | Eastern | 3 | HSD | 327
2023-05-10 21:00 | Eastern | 5 | Hydro | 25
2023-05-10 21:00 | Eastern | 10 | Tripura | 160
2023-05-10 21:00 | Western | 1 | Gas | 961
2023-05-10 21:00 | Western | 2 | HFO | 1009
2023-05-10 21:00 | Western | 3 | HSD | 200
2023-05-10 21:00 | Western | 6 | Coal | 2356
2023-05-10 21:00 | Western | 8 | HVDC | 813
2023-05-10 22:00 | Eastern | 1 | Gas | 5335
2023-05-10 22:00 | Eastern | 2 | HFO | 2728
2023-05-10 22:00 | Eastern | 3 | HSD | 461
2023-05-10 22:00 | Eastern | 5 | Hydro | 25
2023-05-10 22:00 | Eastern | 10 | Tripura | 172
2023-05-10 22:00 | Western | 1 | Gas | 967
2023-05-10 22:00 | Western | 2 | HFO | 1018
2023-05-10 22:00 | Western | 3 | HSD | 0
2023-05-10 22:00 | Western | 6 | Coal | 2372
2023-05-10 22:00 | Western | 8 | HVDC | 817
2023-05-10 23:00 | Eastern | 1 | Gas | 5477
2023-05-10 23:00 | Eastern | 2 | HFO | 2320
2023-05-10 23:00 | Eastern | 3 | HSD | 461
2023-05-10 23:00 | Eastern | 5 | Hydro | 0
2023-05-10 23:00 | Eastern | 10 | Tripura | 176
2023-05-10 23:00 | Western | 1 | Gas | 975
2023-05-10 23:00 | Western | 2 | HFO | 988
2023-05-10 23:00 | Western | 3 | HSD | 0
2023-05-10 23:00 | Western | 6 | Coal | 2237
2023-05-10 23:00 | Western | 8 | HVDC | 817
2023-05-11 | Eastern | 1 | Gas | 5365
2023-05-11 | Eastern | 2 | HFO | 1673
2023-05-11 | Eastern | 3 | HSD | 457
2023-05-11 | Eastern | 5 | Hydro | 0
2023-05-11 | Eastern | 10 | Tripura | 178
2023-05-11 | Western | 1 | Gas | 967
2023-05-11 | Western | 2 | HFO | 966
2023-05-11 | Western | 3 | HSD | 0
2023-05-11 | Western | 6 | Coal | 2327
2023-05-11 | Western | 8 | HVDC | 817
2023-05-11 01:00 | Eastern | 1 | Gas | 5424
2023-05-11 01:00 | Eastern | 2 | HFO | 1288
2023-05-11 01:00 | Eastern | 3 | HSD | 456
2023-05-11 01:00 | Eastern | 10 | Tripura | 182
2023-05-11 01:00 | Western | 1 | Gas | 952
2023-05-11 01:00 | Western | 2 | HFO | 648
2023-05-11 01:00 | Western | 3 | HSD | 0
2023-05-11 01:00 | Western | 6 | Coal | 2412
2023-05-11 01:00 | Western | 8 | HVDC | 862
2023-05-11 02:00 | Eastern | 1 | Gas | 5368
2023-05-11 02:00 | Eastern | 2 | HFO | 1190
2023-05-11 02:00 | Eastern | 3 | HSD | 456
2023-05-11 02:00 | Eastern | 10 | Tripura | 176
2023-05-11 02:00 | Western | 1 | Gas | 967
2023-05-11 02:00 | Western | 2 | HFO | 651
2023-05-11 02:00 | Western | 3 | HSD | 0
2023-05-11 02:00 | Western | 6 | Coal | 2294
2023-05-11 02:00 | Western | 8 | HVDC | 863
2023-05-11 03:00 | Eastern | 1 | Gas | 5336.5
2023-05-11 03:00 | Eastern | 2 | HFO | 1140.2
2023-05-11 03:00 | Eastern | 3 | HSD | 457
2023-05-11 03:00 | Eastern | 10 | Tripura | 174
2023-05-11 03:00 | Western | 1 | Gas | 973
2023-05-11 03:00 | Western | 2 | HFO | 567
2023-05-11 03:00 | Western | 3 | HSD | 0
2023-05-11 03:00 | Western | 6 | Coal | 2318
2023-05-11 03:00 | Western | 8 | HVDC | 919
2023-05-11 04:00 | Eastern | 1 | Gas | 5341
2023-05-11 04:00 | Eastern | 2 | HFO | 1133.2
2023-05-11 04:00 | Eastern | 3 | HSD | 416
2023-05-11 04:00 | Eastern | 10 | Tripura | 172
2023-05-11 04:00 | Western | 1 | Gas | 982
2023-05-11 04:00 | Western | 2 | HFO | 563
2023-05-11 04:00 | Western | 3 | HSD | 0
2023-05-11 04:00 | Western | 6 | Coal | 2326
2023-05-11 04:00 | Western | 8 | HVDC | 920
2023-05-11 05:00 | Eastern | 1 | Gas | 5348
2023-05-11 05:00 | Eastern | 2 | HFO | 1080.2
2023-05-11 05:00 | Eastern | 3 | HSD | 356
2023-05-11 05:00 | Eastern | 10 | Tripura | 170
2023-05-11 05:00 | Western | 1 | Gas | 982
2023-05-11 05:00 | Western | 2 | HFO | 516
2023-05-11 05:00 | Western | 3 | HSD | 0
2023-05-11 05:00 | Western | 6 | Coal | 2329
2023-05-11 05:00 | Western | 8 | HVDC | 920
2023-05-11 06:00 | Eastern | 1 | Gas | 5456
2023-05-11 06:00 | Eastern | 2 | HFO | 1062.2
2023-05-11 06:00 | Eastern | 10 | Tripura | 160
2023-05-11 06:00 | Eastern | 11 | Solar | 6
2023-05-11 06:00 | Western | 1 | Gas | 982
2023-05-11 06:00 | Western | 2 | HFO | 485
2023-05-11 06:00 | Western | 3 | HSD | 0
2023-05-11 06:00 | Western | 6 | Coal | 2311
2023-05-11 06:00 | Western | 8 | HVDC | 920
2023-05-11 06:00 | Western | 11 | Solar | 14.24
2023-05-11 07:00 | Eastern | 1 | Gas | 5270
2023-05-11 07:00 | Eastern | 2 | HFO | 1096.2
2023-05-11 07:00 | Eastern | 10 | Tripura | 156
2023-05-11 07:00 | Eastern | 11 | Solar | 24
2023-05-11 07:00 | Western | 1 | Gas | 988
2023-05-11 07:00 | Western | 2 | HFO | 515
2023-05-11 07:00 | Western | 3 | HSD | 0
2023-05-11 07:00 | Western | 6 | Coal | 2337
2023-05-11 07:00 | Western | 8 | HVDC | 920
2023-05-11 07:00 | Western | 11 | Solar | 62.86
2023-05-11 08:00 | Eastern | 1 | Gas | 5265
2023-05-11 08:00 | Eastern | 2 | HFO | 1123
2023-05-11 08:00 | Eastern | 10 | Tripura | 156
2023-05-11 08:00 | Eastern | 11 | Solar | 47
2023-05-11 08:00 | Western | 1 | Gas | 907
2023-05-11 08:00 | Western | 2 | HFO | 600
2023-05-11 08:00 | Western | 3 | HSD | 0
2023-05-11 08:00 | Western | 6 | Coal | 2297.48
2023-05-11 08:00 | Western | 8 | HVDC | 920
2023-05-11 08:00 | Western | 11 | Solar | 148.12
2023-05-11 09:00 | Eastern | 1 | Gas | 5266
2023-05-11 09:00 | Eastern | 2 | HFO | 1151
2023-05-11 09:00 | Eastern | 10 | Tripura | 150
2023-05-11 09:00 | Eastern | 11 | Solar | 75
2023-05-11 09:00 | Western | 1 | Gas | 927
2023-05-11 09:00 | Western | 2 | HFO | 580
2023-05-11 09:00 | Western | 3 | HSD | 0
2023-05-11 09:00 | Western | 6 | Coal | 2320
2023-05-11 09:00 | Western | 8 | HVDC | 921
2023-05-11 09:00 | Western | 11 | Solar | 201.05
2023-05-11 10:00 | Eastern | 1 | Gas | 5098
2023-05-11 10:00 | Eastern | 2 | HFO | 1537
2023-05-11 10:00 | Eastern | 3 | HSD | 361
2023-05-11 10:00 | Eastern | 5 | Hydro | 18
2023-05-11 10:00 | Eastern | 10 | Tripura | 158
2023-05-11 10:00 | Eastern | 11 | Solar | 85
2023-05-11 10:00 | Western | 1 | Gas | 912
2023-05-11 10:00 | Western | 2 | HFO | 599
2023-05-11 10:00 | Western | 3 | HSD | 0
2023-05-11 10:00 | Western | 6 | Coal | 2364.87
2023-05-11 10:00 | Western | 8 | HVDC | 916
2023-05-11 10:00 | Western | 11 | Solar | 290.11
2023-05-11 11:00 | Eastern | 1 | Gas | 5149
2023-05-11 11:00 | Eastern | 2 | HFO | 1759
2023-05-11 11:00 | Eastern | 3 | HSD | 449
2023-05-11 11:00 | Eastern | 5 | Hydro | 25
2023-05-11 11:00 | Eastern | 10 | Tripura | 160
2023-05-11 11:00 | Eastern | 11 | Solar | 102
2023-05-11 11:00 | Western | 1 | Gas | 906
2023-05-11 11:00 | Western | 2 | HFO | 692
2023-05-11 11:00 | Western | 3 | HSD | 0
2023-05-11 11:00 | Western | 6 | Coal | 2255.73
2023-05-11 11:00 | Western | 8 | HVDC | 917
2023-05-11 11:00 | Western | 11 | Solar | 319.88
2023-05-11 12:00 | Eastern | 1 | Gas | 5091
2023-05-11 12:00 | Eastern | 2 | HFO | 1853
2023-05-11 12:00 | Eastern | 3 | HSD | 456
2023-05-11 12:00 | Eastern | 5 | Hydro | 25
2023-05-11 12:00 | Eastern | 10 | Tripura | 156
2023-05-11 12:00 | Eastern | 11 | Solar | 104.5
2023-05-11 12:00 | Western | 1 | Gas | 880
2023-05-11 12:00 | Western | 2 | HFO | 707
2023-05-11 12:00 | Western | 3 | HSD | 0
2023-05-11 12:00 | Western | 6 | Coal | 2322
2023-05-11 12:00 | Western | 8 | HVDC | 917
2023-05-11 12:00 | Western | 11 | Solar | 325.85
2023-05-11 13:00 | Eastern | 1 | Gas | 5079
2023-05-11 13:00 | Eastern | 2 | HFO | 1920
2023-05-11 13:00 | Eastern | 3 | HSD | 451
2023-05-11 13:00 | Eastern | 5 | Hydro | 25
2023-05-11 13:00 | Eastern | 10 | Tripura | 162
2023-05-11 13:00 | Eastern | 11 | Solar | 100
2023-05-11 13:00 | Western | 1 | Gas | 865
2023-05-11 13:00 | Western | 2 | HFO | 738
2023-05-11 13:00 | Western | 3 | HSD | 0
2023-05-11 13:00 | Western | 6 | Coal | 2310.92
2023-05-11 13:00 | Western | 8 | HVDC | 914
2023-05-11 13:00 | Western | 11 | Solar | 272.78
2023-05-11 14:00 | Eastern | 1 | Gas | 5000
2023-05-11 14:00 | Eastern | 2 | HFO | 1738
2023-05-11 14:00 | Eastern | 3 | HSD | 444
2023-05-11 14:00 | Eastern | 5 | Hydro | 25
2023-05-11 14:00 | Eastern | 10 | Tripura | 154
2023-05-11 14:00 | Eastern | 11 | Solar | 80
2023-05-11 14:00 | Western | 1 | Gas | 767
2023-05-11 14:00 | Western | 2 | HFO | 614
2023-05-11 14:00 | Western | 3 | HSD | 0
2023-05-11 14:00 | Western | 6 | Coal | 2313
2023-05-11 14:00 | Western | 8 | HVDC | 914
2023-05-11 14:00 | Western | 11 | Solar | 247.27
2023-05-11 15:00 | Eastern | 1 | Gas | 4951
2023-05-11 15:00 | Eastern | 2 | HFO | 1736
2023-05-11 15:00 | Eastern | 3 | HSD | 450
2023-05-11 15:00 | Eastern | 5 | Hydro | 25
2023-05-11 15:00 | Eastern | 10 | Tripura | 158
2023-05-11 15:00 | Eastern | 11 | Solar | 50
2023-05-11 15:00 | Western | 1 | Gas | 772
2023-05-11 15:00 | Western | 2 | HFO | 575
2023-05-11 15:00 | Western | 3 | HSD | 25
2023-05-11 15:00 | Western | 6 | Coal | 2311
2023-05-11 15:00 | Western | 8 | HVDC | 915
2023-05-11 15:00 | Western | 11 | Solar | 204.48
2023-05-11 16:00 | Eastern | 1 | Gas | 4928
2023-05-11 16:00 | Eastern | 2 | HFO | 1693
2023-05-11 16:00 | Eastern | 3 | HSD | 194
2023-05-11 16:00 | Eastern | 5 | Hydro | 25
2023-05-11 16:00 | Eastern | 10 | Tripura | 132
2023-05-11 16:00 | Eastern | 11 | Solar | 26
2023-05-11 16:00 | Western | 1 | Gas | 787
2023-05-11 16:00 | Western | 2 | HFO | 612
2023-05-11 16:00 | Western | 3 | HSD | 80
2023-05-11 16:00 | Western | 6 | Coal | 2297
2023-05-11 16:00 | Western | 8 | HVDC | 914
2023-05-11 16:00 | Western | 11 | Solar | 146.84
2023-05-11 17:00 | Eastern | 1 | Gas | 4873
2023-05-11 17:00 | Eastern | 2 | HFO | 1730
2023-05-11 17:00 | Eastern | 3 | HSD | 142
2023-05-11 17:00 | Eastern | 5 | Hydro | 25
2023-05-11 17:00 | Eastern | 10 | Tripura | 132
2023-05-11 17:00 | Eastern | 11 | Solar | 11
2023-05-11 17:00 | Western | 1 | Gas | 783
2023-05-11 17:00 | Western | 2 | HFO | 642
2023-05-11 17:00 | Western | 3 | HSD | 120
2023-05-11 17:00 | Western | 6 | Coal | 2285
2023-05-11 17:00 | Western | 8 | HVDC | 914
2023-05-11 17:00 | Western | 11 | Solar | 67.41
2023-05-11 18:00 | Eastern | 1 | Gas | 4858
2023-05-11 18:00 | Eastern | 2 | HFO | 1915
2023-05-11 18:00 | Eastern | 3 | HSD | 50
2023-05-11 18:00 | Eastern | 5 | Hydro | 25
2023-05-11 18:00 | Eastern | 10 | Tripura | 136
2023-05-11 18:00 | Eastern | 11 | Solar | 1
2023-05-11 18:00 | Western | 1 | Gas | 746
2023-05-11 18:00 | Western | 2 | HFO | 810
2023-05-11 18:00 | Western | 3 | HSD | 0
2023-05-11 18:00 | Western | 6 | Coal | 2216
2023-05-11 18:00 | Western | 8 | HVDC | 914
2023-05-11 18:00 | Western | 11 | Solar | 15.6
2023-05-11 19:00 | Eastern | 1 | Gas | 4885
2023-05-11 19:00 | Eastern | 2 | HFO | 2765
2023-05-11 19:00 | Eastern | 3 | HSD | 259
2023-05-11 19:00 | Eastern | 5 | Hydro | 25
2023-05-11 19:00 | Eastern | 10 | Tripura | 138
2023-05-11 19:00 | Eastern | 11 | Solar | 0
2023-05-11 19:00 | Western | 1 | Gas | 787
2023-05-11 19:00 | Western | 2 | HFO | 987
2023-05-11 19:00 | Western | 3 | HSD | 0
2023-05-11 19:00 | Western | 6 | Coal | 2185
2023-05-11 19:00 | Western | 8 | HVDC | 914
2023-05-11 19:00 | Western | 11 | Solar | 0
2023-05-11 19:30 | Eastern | 1 | Gas | 4757
2023-05-11 19:30 | Eastern | 2 | HFO | 2964
2023-05-11 19:30 | Eastern | 3 | HSD | 206
2023-05-11 19:30 | Eastern | 5 | Hydro | 25
2023-05-11 19:30 | Eastern | 10 | Tripura | 132
2023-05-11 19:30 | Western | 1 | Gas | 727
2023-05-11 19:30 | Western | 2 | HFO | 1038
2023-05-11 19:30 | Western | 3 | HSD | 0
2023-05-11 19:30 | Western | 6 | Coal | 2275
2023-05-11 19:30 | Western | 8 | HVDC | 914
2023-05-11 20:00 | Eastern | 1 | Gas | 4842
2023-05-11 20:00 | Eastern | 2 | HFO | 3049
2023-05-11 20:00 | Eastern | 3 | HSD | 169
2023-05-11 20:00 | Eastern | 5 | Hydro | 25
2023-05-11 20:00 | Eastern | 10 | Tripura | 128
2023-05-11 20:00 | Western | 1 | Gas | 745
2023-05-11 20:00 | Western | 2 | HFO | 1054
2023-05-11 20:00 | Western | 3 | HSD | 0
2023-05-11 20:00 | Western | 6 | Coal | 2303
2023-05-11 20:00 | Western | 8 | HVDC | 804
2023-05-11 21:00 | Eastern | 1 | Gas | 4970
2023-05-11 21:00 | Eastern | 2 | HFO | 2936
2023-05-11 21:00 | Eastern | 3 | HSD | 454
2023-05-11 21:00 | Eastern | 5 | Hydro | 25
2023-05-11 21:00 | Eastern | 10 | Tripura | 140
2023-05-11 21:00 | Western | 1 | Gas | 869
2023-05-11 21:00 | Western | 2 | HFO | 1014
2023-05-11 21:00 | Western | 3 | HSD | 0
2023-05-11 21:00 | Western | 6 | Coal | 2289
2023-05-11 21:00 | Western | 8 | HVDC | 804
2023-05-11 22:00 | Eastern | 1 | Gas | 4998
2023-05-11 22:00 | Eastern | 2 | HFO | 2790
2023-05-11 22:00 | Eastern | 3 | HSD | 453
2023-05-11 22:00 | Eastern | 5 | Hydro | 25
2023-05-11 22:00 | Eastern | 10 | Tripura | 140
2023-05-11 22:00 | Western | 1 | Gas | 859
2023-05-11 22:00 | Western | 2 | HFO | 1009
2023-05-11 22:00 | Western | 3 | HSD | 0
2023-05-11 22:00 | Western | 6 | Coal | 2341
2023-05-11 22:00 | Western | 8 | HVDC | 804
2023-05-11 23:00 | Eastern | 1 | Gas | 5188
2023-05-11 23:00 | Eastern | 2 | HFO | 2414
2023-05-11 23:00 | Eastern | 3 | HSD | 453
2023-05-11 23:00 | Eastern | 10 | Tripura | 148
2023-05-11 23:00 | Western | 1 | Gas | 876
2023-05-11 23:00 | Western | 2 | HFO | 913
2023-05-11 23:00 | Western | 3 | HSD | 0
2023-05-11 23:00 | Western | 6 | Coal | 2357
2023-05-11 23:00 | Western | 8 | HVDC | 803
2023-05-12 | Eastern | 1 | Gas | 5062
2023-05-12 | Eastern | 2 | HFO | 1858
2023-05-12 | Eastern | 3 | HSD | 457
2023-05-12 | Eastern | 10 | Tripura | 148
2023-05-12 | Western | 1 | Gas | 872
2023-05-12 | Western | 2 | HFO | 844
2023-05-12 | Western | 3 | HSD | 0
2023-05-12 | Western | 6 | Coal | 2415
2023-05-12 | Western | 8 | HVDC | 804
2023-05-12 01:00 | Eastern | 1 | Gas | 5157
2023-05-12 01:00 | Eastern | 2 | HFO | 1339
2023-05-12 01:00 | Eastern | 3 | HSD | 459
2023-05-12 01:00 | Eastern | 10 | Tripura | 150
2023-05-12 01:00 | Western | 1 | Gas | 872
2023-05-12 01:00 | Western | 2 | HFO | 650
2023-05-12 01:00 | Western | 3 | HSD | 0
2023-05-12 01:00 | Western | 6 | Coal | 2424
2023-05-12 01:00 | Western | 8 | HVDC | 921
2023-05-12 02:00 | Eastern | 1 | Gas | 5078
2023-05-12 02:00 | Eastern | 2 | HFO | 1318
2023-05-12 02:00 | Eastern | 3 | HSD | 459
2023-05-12 02:00 | Eastern | 10 | Tripura | 152
2023-05-12 02:00 | Western | 1 | Gas | 877
2023-05-12 02:00 | Western | 2 | HFO | 617
2023-05-12 02:00 | Western | 3 | HSD | 0
2023-05-12 02:00 | Western | 6 | Coal | 2428
2023-05-12 02:00 | Western | 8 | HVDC | 921
2023-05-12 03:00 | Eastern | 1 | Gas | 5168
2023-05-12 03:00 | Eastern | 2 | HFO | 1310
2023-05-12 03:00 | Eastern | 3 | HSD | 457
2023-05-12 03:00 | Eastern | 10 | Tripura | 150
2023-05-12 03:00 | Western | 1 | Gas | 890
2023-05-12 03:00 | Western | 2 | HFO | 515
2023-05-12 03:00 | Western | 3 | HSD | 0
2023-05-12 03:00 | Western | 6 | Coal | 2425
2023-05-12 03:00 | Western | 8 | HVDC | 920
2023-05-12 04:00 | Eastern | 1 | Gas | 5127
2023-05-12 04:00 | Eastern | 2 | HFO | 1263
2023-05-12 04:00 | Eastern | 3 | HSD | 425
2023-05-12 04:00 | Eastern | 10 | Tripura | 150
2023-05-12 04:00 | Western | 1 | Gas | 891
2023-05-12 04:00 | Western | 2 | HFO | 504
2023-05-12 04:00 | Western | 3 | HSD | 0
2023-05-12 04:00 | Western | 6 | Coal | 2445
2023-05-12 04:00 | Western | 8 | HVDC | 921
2023-05-12 05:00 | Eastern | 1 | Gas | 5102
2023-05-12 05:00 | Eastern | 2 | HFO | 1199
2023-05-12 05:00 | Eastern | 3 | HSD | 314
2023-05-12 05:00 | Eastern | 10 | Tripura | 146
2023-05-12 05:00 | Western | 1 | Gas | 889
2023-05-12 05:00 | Western | 2 | HFO | 456
2023-05-12 05:00 | Western | 3 | HSD | 0
2023-05-12 05:00 | Western | 6 | Coal | 2443
2023-05-12 05:00 | Western | 8 | HVDC | 921
2023-05-12 06:00 | Eastern | 1 | Gas | 5049
2023-05-12 06:00 | Eastern | 2 | HFO | 1162
2023-05-12 06:00 | Eastern | 3 | HSD | 34
2023-05-12 06:00 | Eastern | 10 | Tripura | 134
2023-05-12 06:00 | Eastern | 11 | Solar | 4
2023-05-12 06:00 | Western | 1 | Gas | 866
2023-05-12 06:00 | Western | 2 | HFO | 384
2023-05-12 06:00 | Western | 3 | HSD | 0
2023-05-12 06:00 | Western | 6 | Coal | 2431
2023-05-12 06:00 | Western | 8 | HVDC | 921
2023-05-12 06:00 | Western | 11 | Solar | 11.24
2023-05-12 07:00 | Eastern | 1 | Gas | 4941
2023-05-12 07:00 | Eastern | 2 | HFO | 1121
2023-05-12 07:00 | Eastern | 10 | Tripura | 132
2023-05-12 07:00 | Eastern | 11 | Solar | 20
2023-05-12 07:00 | Western | 1 | Gas | 853
2023-05-12 07:00 | Western | 2 | HFO | 373
2023-05-12 07:00 | Western | 3 | HSD | 0
2023-05-12 07:00 | Western | 6 | Coal | 2440
2023-05-12 07:00 | Western | 8 | HVDC | 920
2023-05-12 07:00 | Western | 11 | Solar | 60.67
2023-05-12 08:00 | Eastern | 1 | Gas | 4886
2023-05-12 08:00 | Eastern | 2 | HFO | 1143
2023-05-12 08:00 | Eastern | 10 | Tripura | 132
2023-05-12 08:00 | Eastern | 11 | Solar | 43
2023-05-12 08:00 | Western | 1 | Gas | 793
2023-05-12 08:00 | Western | 2 | HFO | 378
2023-05-12 08:00 | Western | 3 | HSD | 0
2023-05-12 08:00 | Western | 6 | Coal | 2434
2023-05-12 08:00 | Western | 8 | HVDC | 921
2023-05-12 08:00 | Western | 11 | Solar | 136.6
2023-05-12 09:00 | Eastern | 1 | Gas | 4713
2023-05-12 09:00 | Eastern | 2 | HFO | 1153
2023-05-12 09:00 | Eastern | 10 | Tripura | 136
2023-05-12 09:00 | Eastern | 11 | Solar | 53
2023-05-12 09:00 | Western | 1 | Gas | 849
2023-05-12 09:00 | Western | 2 | HFO | 266
2023-05-12 09:00 | Western | 3 | HSD | 50
2023-05-12 09:00 | Western | 6 | Coal | 2414
2023-05-12 09:00 | Western | 8 | HVDC | 921
2023-05-12 09:00 | Western | 11 | Solar | 229.19
2023-05-12 10:00 | Eastern | 1 | Gas | 4706
2023-05-12 10:00 | Eastern | 2 | HFO | 1282
2023-05-12 10:00 | Eastern | 5 | Hydro | 0
2023-05-12 10:00 | Eastern | 10 | Tripura | 140
2023-05-12 10:00 | Eastern | 11 | Solar | 59
2023-05-12 10:00 | Western | 1 | Gas | 845
2023-05-12 10:00 | Western | 2 | HFO | 262
2023-05-12 10:00 | Western | 3 | HSD | 190
2023-05-12 10:00 | Western | 6 | Coal | 2380
2023-05-12 10:00 | Western | 8 | HVDC | 920
2023-05-12 10:00 | Western | 11 | Solar | 215.48
2023-05-12 11:00 | Eastern | 1 | Gas | 4680
2023-05-12 11:00 | Eastern | 2 | HFO | 1486
2023-05-12 11:00 | Eastern | 5 | Hydro | 27
2023-05-12 11:00 | Eastern | 10 | Tripura | 138
2023-05-12 11:00 | Eastern | 11 | Solar | 61
2023-05-12 11:00 | Western | 1 | Gas | 785
2023-05-12 11:00 | Western | 2 | HFO | 273
2023-05-12 11:00 | Western | 3 | HSD | 230
2023-05-12 11:00 | Western | 6 | Coal | 2324
2023-05-12 11:00 | Western | 8 | HVDC | 922
2023-05-12 11:00 | Western | 11 | Solar | 294.04
2023-05-12 12:00 | Eastern | 1 | Gas | 5048
2023-05-12 12:00 | Eastern | 2 | HFO | 1558
2023-05-12 12:00 | Eastern | 3 | HSD | 0
2023-05-12 12:00 | Eastern | 5 | Hydro | 27
2023-05-12 12:00 | Eastern | 10 | Tripura | 146
2023-05-12 12:00 | Eastern | 11 | Solar | 63
2023-05-12 12:00 | Western | 1 | Gas | 838
2023-05-12 12:00 | Western | 2 | HFO | 384
2023-05-12 12:00 | Western | 3 | HSD | 150
2023-05-12 12:00 | Western | 6 | Coal | 2356
2023-05-12 12:00 | Western | 8 | HVDC | 921
2023-05-12 12:00 | Western | 11 | Solar | 273.57
2023-05-12 13:00 | Eastern | 1 | Gas | 4966
2023-05-12 13:00 | Eastern | 2 | HFO | 1637
2023-05-12 13:00 | Eastern | 3 | HSD | 180
2023-05-12 13:00 | Eastern | 5 | Hydro | 27
2023-05-12 13:00 | Eastern | 10 | Tripura | 150
2023-05-12 13:00 | Eastern | 11 | Solar | 66
2023-05-12 13:00 | Western | 1 | Gas | 850
2023-05-12 13:00 | Western | 2 | HFO | 501
2023-05-12 13:00 | Western | 3 | HSD | 200
2023-05-12 13:00 | Western | 6 | Coal | 2463
2023-05-12 13:00 | Western | 8 | HVDC | 921
2023-05-12 13:00 | Western | 11 | Solar | 306.05
2023-05-12 14:00 | Eastern | 1 | Gas | 5003
2023-05-12 14:00 | Eastern | 2 | HFO | 1646
2023-05-12 14:00 | Eastern | 3 | HSD | 0
2023-05-12 14:00 | Eastern | 5 | Hydro | 27
2023-05-12 14:00 | Eastern | 10 | Tripura | 152
2023-05-12 14:00 | Eastern | 11 | Solar | 60
2023-05-12 14:00 | Western | 1 | Gas | 815
2023-05-12 14:00 | Western | 2 | HFO | 555
2023-05-12 14:00 | Western | 3 | HSD | 0
2023-05-12 14:00 | Western | 6 | Coal | 2457
2023-05-12 14:00 | Western | 8 | HVDC | 921
2023-05-12 14:00 | Western | 11 | Solar | 194.11
2023-05-12 15:00 | Eastern | 1 | Gas | 5035
2023-05-12 15:00 | Eastern | 2 | HFO | 1651
2023-05-12 15:00 | Eastern | 5 | Hydro | 27
2023-05-12 15:00 | Eastern | 10 | Tripura | 158
2023-05-12 15:00 | Eastern | 11 | Solar | 59
2023-05-12 15:00 | Western | 1 | Gas | 835
2023-05-12 15:00 | Western | 2 | HFO | 571
2023-05-12 15:00 | Western | 3 | HSD | 0
2023-05-12 15:00 | Western | 6 | Coal | 2434
2023-05-12 15:00 | Western | 8 | HVDC | 920
2023-05-12 15:00 | Western | 11 | Solar | 200.42
2023-05-12 16:00 | Eastern | 1 | Gas | 5037
2023-05-12 16:00 | Eastern | 2 | HFO | 1578
2023-05-12 16:00 | Eastern | 5 | Hydro | 27
2023-05-12 16:00 | Eastern | 10 | Tripura | 124
2023-05-12 16:00 | Eastern | 11 | Solar | 40
2023-05-12 16:00 | Western | 1 | Gas | 833
2023-05-12 16:00 | Western | 2 | HFO | 597
2023-05-12 16:00 | Western | 3 | HSD | 0
2023-05-12 16:00 | Western | 6 | Coal | 2458
2023-05-12 16:00 | Western | 8 | HVDC | 763
2023-05-12 16:00 | Western | 11 | Solar | 119.57
2023-05-12 17:00 | Eastern | 1 | Gas | 4990
2023-05-12 17:00 | Eastern | 2 | HFO | 1693
2023-05-12 17:00 | Eastern | 5 | Hydro | 27
2023-05-12 17:00 | Eastern | 10 | Tripura | 130
2023-05-12 17:00 | Eastern | 11 | Solar | 13
2023-05-12 17:00 | Western | 1 | Gas | 734
2023-05-12 17:00 | Western | 2 | HFO | 634
2023-05-12 17:00 | Western | 3 | HSD | 0
2023-05-12 17:00 | Western | 6 | Coal | 2341
2023-05-12 17:00 | Western | 8 | HVDC | 763
2023-05-12 17:00 | Western | 11 | Solar | 47.67
2023-05-12 18:00 | Eastern | 1 | Gas | 4715
2023-05-12 18:00 | Eastern | 2 | HFO | 2013
2023-05-12 18:00 | Eastern | 3 | HSD | 0
2023-05-12 18:00 | Eastern | 5 | Hydro | 27
2023-05-12 18:00 | Eastern | 10 | Tripura | 126
2023-05-12 18:00 | Eastern | 11 | Solar | 3
2023-05-12 18:00 | Western | 1 | Gas | 701
2023-05-12 18:00 | Western | 2 | HFO | 791
2023-05-12 18:00 | Western | 3 | HSD | 0
2023-05-12 18:00 | Western | 6 | Coal | 2212
2023-05-12 18:00 | Western | 8 | HVDC | 764
2023-05-12 18:00 | Western | 11 | Solar | 13.17
2023-05-12 19:00 | Eastern | 1 | Gas | 5008
2023-05-12 19:00 | Eastern | 2 | HFO | 2872
2023-05-12 19:00 | Eastern | 3 | HSD | 125
2023-05-12 19:00 | Eastern | 5 | Hydro | 27
2023-05-12 19:00 | Eastern | 10 | Tripura | 130
2023-05-12 19:00 | Eastern | 11 | Solar | 0
2023-05-12 19:00 | Western | 1 | Gas | 940
2023-05-12 19:00 | Western | 2 | HFO | 862
2023-05-12 19:00 | Western | 3 | HSD | 0
2023-05-12 19:00 | Western | 6 | Coal | 2296.25
2023-05-12 19:00 | Western | 8 | HVDC | 764
2023-05-12 19:00 | Western | 11 | Solar | 0
2023-05-12 19:30 | Eastern | 1 | Gas | 5117
2023-05-12 19:30 | Eastern | 2 | HFO | 3066
2023-05-12 19:30 | Eastern | 3 | HSD | 169
2023-05-12 19:30 | Eastern | 5 | Hydro | 27
2023-05-12 19:30 | Eastern | 10 | Tripura | 138
2023-05-12 19:30 | Western | 1 | Gas | 971
2023-05-12 19:30 | Western | 2 | HFO | 963
2023-05-12 19:30 | Western | 3 | HSD | 0
2023-05-12 19:30 | Western | 6 | Coal | 2458
2023-05-12 19:30 | Western | 8 | HVDC | 763
2023-05-12 20:00 | Eastern | 1 | Gas | 5130
2023-05-12 20:00 | Eastern | 2 | HFO | 3126
2023-05-12 20:00 | Eastern | 3 | HSD | 257
2023-05-12 20:00 | Eastern | 5 | Hydro | 27
2023-05-12 20:00 | Eastern | 10 | Tripura | 140
2023-05-12 20:00 | Western | 1 | Gas | 990
2023-05-12 20:00 | Western | 2 | HFO | 1057
2023-05-12 20:00 | Western | 3 | HSD | 0
2023-05-12 20:00 | Western | 6 | Coal | 2410
2023-05-12 20:00 | Western | 8 | HVDC | 669
2023-05-12 21:00 | Eastern | 1 | Gas | 5117
2023-05-12 21:00 | Eastern | 2 | HFO | 3045
2023-05-12 21:00 | Eastern | 3 | HSD | 264
2023-05-12 21:00 | Eastern | 5 | Hydro | 27
2023-05-12 21:00 | Eastern | 10 | Tripura | 128
2023-05-12 21:00 | Western | 1 | Gas | 992
2023-05-12 21:00 | Western | 2 | HFO | 1053
2023-05-12 21:00 | Western | 3 | HSD | 0
2023-05-12 21:00 | Western | 6 | Coal | 2485
2023-05-12 21:00 | Western | 8 | HVDC | 668
2023-05-12 22:00 | Eastern | 1 | Gas | 5118
2023-05-12 22:00 | Eastern | 2 | HFO | 2825
2023-05-12 22:00 | Eastern | 3 | HSD | 442
2023-05-12 22:00 | Eastern | 5 | Hydro | 27
2023-05-12 22:00 | Eastern | 10 | Tripura | 138
2023-05-12 22:00 | Western | 1 | Gas | 1001
2023-05-12 22:00 | Western | 2 | HFO | 1008
2023-05-12 22:00 | Western | 3 | HSD | 0
2023-05-12 22:00 | Western | 6 | Coal | 2518.82
2023-05-12 22:00 | Western | 8 | HVDC | 669
2023-05-12 23:00 | Eastern | 1 | Gas | 5157
2023-05-12 23:00 | Eastern | 2 | HFO | 2183
2023-05-12 23:00 | Eastern | 3 | HSD | 450
2023-05-12 23:00 | Eastern | 5 | Hydro | 0
2023-05-12 23:00 | Eastern | 10 | Tripura | 140
2023-05-12 23:00 | Western | 1 | Gas | 993
2023-05-12 23:00 | Western | 2 | HFO | 734
2023-05-12 23:00 | Western | 3 | HSD | 0
2023-05-12 23:00 | Western | 6 | Coal | 2136
2023-05-12 23:00 | Western | 8 | HVDC | 668
2023-05-13 | Eastern | 1 | Gas | 5020
2023-05-13 | Eastern | 2 | HFO | 1836
2023-05-13 | Eastern | 3 | HSD | 112
2023-05-13 | Eastern | 10 | Tripura | 120
2023-05-13 | Western | 1 | Gas | 914
2023-05-13 | Western | 2 | HFO | 683
2023-05-13 | Western | 3 | HSD | 0
2023-05-13 | Western | 6 | Coal | 2277
2023-05-13 | Western | 8 | HVDC | 826
2023-05-13 01:00 | Eastern | 1 | Gas | 4768
2023-05-13 01:00 | Eastern | 2 | HFO | 1310
2023-05-13 01:00 | Eastern | 3 | HSD | 311
2023-05-13 01:00 | Eastern | 10 | Tripura | 120
2023-05-13 01:00 | Western | 1 | Gas | 905
2023-05-13 01:00 | Western | 2 | HFO | 595
2023-05-13 01:00 | Western | 3 | HSD | 0
2023-05-13 01:00 | Western | 6 | Coal | 2285
2023-05-13 01:00 | Western | 8 | HVDC | 827
2023-05-13 02:00 | Eastern | 1 | Gas | 4679
2023-05-13 02:00 | Eastern | 2 | HFO | 1302
2023-05-13 02:00 | Eastern | 3 | HSD | 363
2023-05-13 02:00 | Eastern | 10 | Tripura | 130
2023-05-13 02:00 | Western | 1 | Gas | 1002
2023-05-13 02:00 | Western | 2 | HFO | 564
2023-05-13 02:00 | Western | 3 | HSD | 0
2023-05-13 02:00 | Western | 6 | Coal | 2309
2023-05-13 02:00 | Western | 8 | HVDC | 827
2023-05-13 03:00 | Eastern | 1 | Gas | 4555
2023-05-13 03:00 | Eastern | 2 | HFO | 1251
2023-05-13 03:00 | Eastern | 3 | HSD | 367
2023-05-13 03:00 | Eastern | 10 | Tripura | 124
2023-05-13 03:00 | Western | 1 | Gas | 1003
2023-05-13 03:00 | Western | 2 | HFO | 495
2023-05-13 03:00 | Western | 3 | HSD | 0
2023-05-13 03:00 | Western | 6 | Coal | 2329
2023-05-13 03:00 | Western | 8 | HVDC | 922
2023-05-13 04:00 | Eastern | 1 | Gas | 4450
2023-05-13 04:00 | Eastern | 2 | HFO | 1142
2023-05-13 04:00 | Eastern | 3 | HSD | 457
2023-05-13 04:00 | Eastern | 10 | Tripura | 128
2023-05-13 04:00 | Western | 1 | Gas | 1006
2023-05-13 04:00 | Western | 2 | HFO | 489
2023-05-13 04:00 | Western | 3 | HSD | 0
2023-05-13 04:00 | Western | 6 | Coal | 2380
2023-05-13 04:00 | Western | 8 | HVDC | 921
2023-05-13 05:00 | Eastern | 1 | Gas | 4413
2023-05-13 05:00 | Eastern | 2 | HFO | 1118
2023-05-13 05:00 | Eastern | 3 | HSD | 275
2023-05-13 05:00 | Eastern | 10 | Tripura | 134
2023-05-13 05:00 | Eastern | 11 | Solar | 0
2023-05-13 05:00 | Western | 1 | Gas | 1008
2023-05-13 05:00 | Western | 2 | HFO | 462
2023-05-13 05:00 | Western | 3 | HSD | 0
2023-05-13 05:00 | Western | 6 | Coal | 2407
2023-05-13 05:00 | Western | 8 | HVDC | 922
2023-05-13 05:00 | Western | 11 | Solar | 0
2023-05-13 06:00 | Eastern | 1 | Gas | 4322
2023-05-13 06:00 | Eastern | 2 | HFO | 1107
2023-05-13 06:00 | Eastern | 3 | HSD | 100
2023-05-13 06:00 | Eastern | 10 | Tripura | 134
2023-05-13 06:00 | Eastern | 11 | Solar | 5
2023-05-13 06:00 | Western | 1 | Gas | 1001
2023-05-13 06:00 | Western | 2 | HFO | 499
2023-05-13 06:00 | Western | 3 | HSD | 0
2023-05-13 06:00 | Western | 6 | Coal | 2338
2023-05-13 06:00 | Western | 8 | HVDC | 922
2023-05-13 06:00 | Western | 11 | Solar | 15
2023-05-13 07:00 | Eastern | 1 | Gas | 4094
2023-05-13 07:00 | Eastern | 2 | HFO | 1092
2023-05-13 07:00 | Eastern | 3 | HSD | 50
2023-05-13 07:00 | Eastern | 10 | Tripura | 134
2023-05-13 07:00 | Eastern | 11 | Solar | 15
2023-05-13 07:00 | Western | 1 | Gas | 969
2023-05-13 07:00 | Western | 2 | HFO | 503
2023-05-13 07:00 | Western | 3 | HSD | 0
2023-05-13 07:00 | Western | 6 | Coal | 2330
2023-05-13 07:00 | Western | 8 | HVDC | 922
2023-05-13 07:00 | Western | 11 | Solar | 64.81
2023-05-13 08:00 | Eastern | 1 | Gas | 3988
2023-05-13 08:00 | Eastern | 2 | HFO | 1024
2023-05-13 08:00 | Eastern | 3 | HSD | 50
2023-05-13 08:00 | Eastern | 5 | Hydro | 0
2023-05-13 08:00 | Eastern | 10 | Tripura | 132
2023-05-13 08:00 | Eastern | 11 | Solar | 31
2023-05-13 08:00 | Western | 1 | Gas | 948
2023-05-13 08:00 | Western | 2 | HFO | 557
2023-05-13 08:00 | Western | 3 | HSD | 0
2023-05-13 08:00 | Western | 6 | Coal | 2175
2023-05-13 08:00 | Western | 8 | HVDC | 921
2023-05-13 08:00 | Western | 11 | Solar | 115.56
2023-05-13 09:00 | Eastern | 1 | Gas | 3877
2023-05-13 09:00 | Eastern | 2 | HFO | 1043
2023-05-13 09:00 | Eastern | 3 | HSD | 50
2023-05-13 09:00 | Eastern | 5 | Hydro | 25
2023-05-13 09:00 | Eastern | 10 | Tripura | 118
2023-05-13 09:00 | Eastern | 11 | Solar | 56
2023-05-13 09:00 | Western | 1 | Gas | 897
2023-05-13 09:00 | Western | 2 | HFO | 519
2023-05-13 09:00 | Western | 3 | HSD | 0
2023-05-13 09:00 | Western | 6 | Coal | 2066
2023-05-13 09:00 | Western | 8 | HVDC | 922
2023-05-13 09:00 | Western | 11 | Solar | 193.99
2023-05-13 10:00 | Eastern | 1 | Gas | 3850
2023-05-13 10:00 | Eastern | 2 | HFO | 1170.5
2023-05-13 10:00 | Eastern | 3 | HSD | 50
2023-05-13 10:00 | Eastern | 5 | Hydro | 30
2023-05-13 10:00 | Eastern | 10 | Tripura | 132
2023-05-13 10:00 | Eastern | 11 | Solar | 64
2023-05-13 10:00 | Western | 1 | Gas | 930
2023-05-13 10:00 | Western | 2 | HFO | 538
2023-05-13 10:00 | Western | 3 | HSD | 0
2023-05-13 10:00 | Western | 6 | Coal | 2089
2023-05-13 10:00 | Western | 8 | HVDC | 922
2023-05-13 10:00 | Western | 11 | Solar | 235.81
2023-05-13 11:00 | Eastern | 1 | Gas | 3919
2023-05-13 11:00 | Eastern | 2 | HFO | 1307
2023-05-13 11:00 | Eastern | 3 | HSD | 194
2023-05-13 11:00 | Eastern | 5 | Hydro | 30
2023-05-13 11:00 | Eastern | 10 | Tripura | 128
2023-05-13 11:00 | Eastern | 11 | Solar | 84
2023-05-13 11:00 | Western | 1 | Gas | 939
2023-05-13 11:00 | Western | 2 | HFO | 572
2023-05-13 11:00 | Western | 3 | HSD | 0
2023-05-13 11:00 | Western | 6 | Coal | 2023
2023-05-13 11:00 | Western | 8 | HVDC | 922
2023-05-13 11:00 | Western | 11 | Solar | 238.14
2023-05-13 12:00 | Eastern | 1 | Gas | 3894
2023-05-13 12:00 | Eastern | 2 | HFO | 1366
2023-05-13 12:00 | Eastern | 3 | HSD | 371
2023-05-13 12:00 | Eastern | 5 | Hydro | 30
2023-05-13 12:00 | Eastern | 10 | Tripura | 142
2023-05-13 12:00 | Eastern | 11 | Solar | 85
2023-05-13 12:00 | Western | 1 | Gas | 925
2023-05-13 12:00 | Western | 2 | HFO | 588
2023-05-13 12:00 | Western | 3 | HSD | 0
2023-05-13 12:00 | Western | 6 | Coal | 2117
2023-05-13 12:00 | Western | 8 | HVDC | 923
2023-05-13 12:00 | Western | 11 | Solar | 308.78
2023-05-13 13:00 | Eastern | 1 | Gas | 3890
2023-05-13 13:00 | Eastern | 2 | HFO | 1472
2023-05-13 13:00 | Eastern | 3 | HSD | 463
2023-05-13 13:00 | Eastern | 5 | Hydro | 30
2023-05-13 13:00 | Eastern | 10 | Tripura | 136
2023-05-13 13:00 | Eastern | 11 | Solar | 92
2023-05-13 13:00 | Western | 1 | Gas | 901
2023-05-13 13:00 | Western | 2 | HFO | 581
2023-05-13 13:00 | Western | 3 | HSD | 0
2023-05-13 13:00 | Western | 6 | Coal | 2079
2023-05-13 13:00 | Western | 8 | HVDC | 921
2023-05-13 13:00 | Western | 11 | Solar | 246
2023-05-13 14:00 | Eastern | 1 | Gas | 3832
2023-05-13 14:00 | Eastern | 2 | HFO | 1483
2023-05-13 14:00 | Eastern | 3 | HSD | 340
2023-05-13 14:00 | Eastern | 5 | Hydro | 30
2023-05-13 14:00 | Eastern | 10 | Tripura | 118
2023-05-13 14:00 | Eastern | 11 | Solar | 64
2023-05-13 14:00 | Western | 1 | Gas | 883
2023-05-13 14:00 | Western | 2 | HFO | 593
2023-05-13 14:00 | Western | 3 | HSD | 0
2023-05-13 14:00 | Western | 6 | Coal | 2099
2023-05-13 14:00 | Western | 8 | HVDC | 923
2023-05-13 14:00 | Western | 11 | Solar | 257
2023-05-13 15:00 | Eastern | 1 | Gas | 3786
2023-05-13 15:00 | Eastern | 2 | HFO | 1559
2023-05-13 15:00 | Eastern | 3 | HSD | 191
2023-05-13 15:00 | Eastern | 5 | Hydro | 30
2023-05-13 15:00 | Eastern | 10 | Tripura | 136
2023-05-13 15:00 | Eastern | 11 | Solar | 49
2023-05-13 15:00 | Western | 1 | Gas | 870
2023-05-13 15:00 | Western | 2 | HFO | 619
2023-05-13 15:00 | Western | 3 | HSD | 0
2023-05-13 15:00 | Western | 6 | Coal | 2100
2023-05-13 15:00 | Western | 8 | HVDC | 922
2023-05-13 15:00 | Western | 11 | Solar | 182.92
2023-05-13 16:00 | Eastern | 1 | Gas | 3732
2023-05-13 16:00 | Eastern | 2 | HFO | 1593
2023-05-13 16:00 | Eastern | 3 | HSD | 461
2023-05-13 16:00 | Eastern | 5 | Hydro | 30
2023-05-13 16:00 | Eastern | 10 | Tripura | 120
2023-05-13 16:00 | Eastern | 11 | Solar | 33
2023-05-13 16:00 | Western | 1 | Gas | 847
2023-05-13 16:00 | Western | 2 | HFO | 592
2023-05-13 16:00 | Western | 3 | HSD | 0
2023-05-13 16:00 | Western | 6 | Coal | 2168
2023-05-13 16:00 | Western | 8 | HVDC | 921
2023-05-13 16:00 | Western | 11 | Solar | 110.3
2023-05-13 17:00 | Eastern | 1 | Gas | 3691
2023-05-13 17:00 | Eastern | 2 | HFO | 1687
2023-05-13 17:00 | Eastern | 3 | HSD | 307
2023-05-13 17:00 | Eastern | 5 | Hydro | 30
2023-05-13 17:00 | Eastern | 10 | Tripura | 122
2023-05-13 17:00 | Eastern | 11 | Solar | 18
2023-05-13 17:00 | Western | 1 | Gas | 844
2023-05-13 17:00 | Western | 2 | HFO | 605
2023-05-13 17:00 | Western | 3 | HSD | 0
2023-05-13 17:00 | Western | 6 | Coal | 2207
2023-05-13 17:00 | Western | 8 | HVDC | 921
2023-05-13 17:00 | Western | 11 | Solar | 49.03
2023-05-13 18:00 | Eastern | 1 | Gas | 3680
2023-05-13 18:00 | Eastern | 2 | HFO | 1987
2023-05-13 18:00 | Eastern | 3 | HSD | 230
2023-05-13 18:00 | Eastern | 5 | Hydro | 30
2023-05-13 18:00 | Eastern | 10 | Tripura | 126
2023-05-13 18:00 | Eastern | 11 | Solar | 3
2023-05-13 18:00 | Western | 1 | Gas | 850
2023-05-13 18:00 | Western | 2 | HFO | 617
2023-05-13 18:00 | Western | 3 | HSD | 0
2023-05-13 18:00 | Western | 6 | Coal | 2200
2023-05-13 18:00 | Western | 8 | HVDC | 920
2023-05-13 18:00 | Western | 11 | Solar | 11.2
2023-05-13 19:00 | Eastern | 1 | Gas | 3714
2023-05-13 19:00 | Eastern | 2 | HFO | 2700
2023-05-13 19:00 | Eastern | 3 | HSD | 376
2023-05-13 19:00 | Eastern | 5 | Hydro | 30
2023-05-13 19:00 | Eastern | 10 | Tripura | 122
2023-05-13 19:00 | Western | 1 | Gas | 858
2023-05-13 19:00 | Western | 2 | HFO | 781
2023-05-13 19:00 | Western | 3 | HSD | 0
2023-05-13 19:00 | Western | 6 | Coal | 2198
2023-05-13 19:00 | Western | 8 | HVDC | 921
2023-05-13 19:30 | Eastern | 1 | Gas | 3714
2023-05-13 19:30 | Eastern | 2 | HFO | 2779
2023-05-13 19:30 | Eastern | 3 | HSD | 376
2023-05-13 19:30 | Eastern | 5 | Hydro | 30
2023-05-13 19:30 | Eastern | 10 | Tripura | 130
2023-05-13 19:30 | Western | 1 | Gas | 878
2023-05-13 19:30 | Western | 2 | HFO | 981
2023-05-13 19:30 | Western | 3 | HSD | 0
2023-05-13 19:30 | Western | 6 | Coal | 2284
2023-05-13 19:30 | Western | 8 | HVDC | 921
2023-05-13 20:00 | Eastern | 1 | Gas | 3722
2023-05-13 20:00 | Eastern | 2 | HFO | 2836
2023-05-13 20:00 | Eastern | 3 | HSD | 377
2023-05-13 20:00 | Eastern | 5 | Hydro | 30
2023-05-13 20:00 | Eastern | 10 | Tripura | 112
2023-05-13 20:00 | Western | 1 | Gas | 880
2023-05-13 20:00 | Western | 2 | HFO | 1055
2023-05-13 20:00 | Western | 3 | HSD | 0
2023-05-13 20:00 | Western | 6 | Coal | 2290
2023-05-13 20:00 | Western | 8 | HVDC | 819
2023-05-13 21:00 | Eastern | 1 | Gas | 3776
2023-05-13 21:00 | Eastern | 2 | HFO | 2851
2023-05-13 21:00 | Eastern | 3 | HSD | 468
2023-05-13 21:00 | Eastern | 5 | Hydro | 30
2023-05-13 21:00 | Eastern | 10 | Tripura | 118
2023-05-13 21:00 | Western | 1 | Gas | 891
2023-05-13 21:00 | Western | 2 | HFO | 1106
2023-05-13 21:00 | Western | 3 | HSD | 0
2023-05-13 21:00 | Western | 6 | Coal | 2290
2023-05-13 21:00 | Western | 8 | HVDC | 819
2023-05-13 22:00 | Eastern | 1 | Gas | 3733
2023-05-13 22:00 | Eastern | 2 | HFO | 2567
2023-05-13 22:00 | Eastern | 3 | HSD | 463
2023-05-13 22:00 | Eastern | 5 | Hydro | 30
2023-05-13 22:00 | Eastern | 10 | Tripura | 114
2023-05-13 22:00 | Western | 1 | Gas | 910
2023-05-13 22:00 | Western | 2 | HFO | 1047
2023-05-13 22:00 | Western | 3 | HSD | 0
2023-05-13 22:00 | Western | 6 | Coal | 2289
2023-05-13 22:00 | Western | 8 | HVDC | 819
2023-05-13 23:00 | Eastern | 1 | Gas | 3771
2023-05-13 23:00 | Eastern | 2 | HFO | 2014
2023-05-13 23:00 | Eastern | 3 | HSD | 464
2023-05-13 23:00 | Eastern | 5 | Hydro | 0
2023-05-13 23:00 | Eastern | 10 | Tripura | 132
2023-05-13 23:00 | Western | 1 | Gas | 901
2023-05-13 23:00 | Western | 2 | HFO | 901
2023-05-13 23:00 | Western | 3 | HSD | 0
2023-05-13 23:00 | Western | 6 | Coal | 2289
2023-05-13 23:00 | Western | 8 | HVDC | 819
2023-05-14 | Eastern | 1 | Gas | 3754
2023-05-14 | Eastern | 2 | HFO | 1590
2023-05-14 | Eastern | 3 | HSD | 456
2023-05-14 | Eastern | 10 | Tripura | 136
2023-05-14 | Western | 1 | Gas | 896
2023-05-14 | Western | 2 | HFO | 696
2023-05-14 | Western | 3 | HSD | 0
2023-05-14 | Western | 6 | Coal | 2289
2023-05-14 | Western | 8 | HVDC | 820
2023-05-14 01:00 | Eastern | 1 | Gas | 3747
2023-05-14 01:00 | Eastern | 2 | HFO | 1349
2023-05-14 01:00 | Eastern | 3 | HSD | 457
2023-05-14 01:00 | Eastern | 10 | Tripura | 128
2023-05-14 01:00 | Western | 1 | Gas | 894
2023-05-14 01:00 | Western | 2 | HFO | 629
2023-05-14 01:00 | Western | 3 | HSD | 0
2023-05-14 01:00 | Western | 6 | Coal | 2290
2023-05-14 01:00 | Western | 8 | HVDC | 915
2023-05-14 02:00 | Eastern | 1 | Gas | 3726
2023-05-14 02:00 | Eastern | 2 | HFO | 1095
2023-05-14 02:00 | Eastern | 3 | HSD | 450
2023-05-14 02:00 | Eastern | 10 | Tripura | 122
2023-05-14 02:00 | Western | 1 | Gas | 895
2023-05-14 02:00 | Western | 2 | HFO | 629
2023-05-14 02:00 | Western | 3 | HSD | 0
2023-05-14 02:00 | Western | 6 | Coal | 2290
2023-05-14 02:00 | Western | 8 | HVDC | 860
2023-05-14 03:00 | Eastern | 1 | Gas | 3711
2023-05-14 03:00 | Eastern | 2 | HFO | 1075
2023-05-14 03:00 | Eastern | 3 | HSD | 456
2023-05-14 03:00 | Eastern | 10 | Tripura | 130
2023-05-14 03:00 | Western | 1 | Gas | 903
2023-05-14 03:00 | Western | 2 | HFO | 554
2023-05-14 03:00 | Western | 3 | HSD | 0
2023-05-14 03:00 | Western | 6 | Coal | 2288
2023-05-14 03:00 | Western | 8 | HVDC | 860
2023-05-14 04:00 | Eastern | 1 | Gas | 3704
2023-05-14 04:00 | Eastern | 2 | HFO | 982
2023-05-14 04:00 | Eastern | 3 | HSD | 455
2023-05-14 04:00 | Eastern | 10 | Tripura | 132
2023-05-14 04:00 | Western | 1 | Gas | 906
2023-05-14 04:00 | Western | 2 | HFO | 556
2023-05-14 04:00 | Western | 3 | HSD | 0
2023-05-14 04:00 | Western | 6 | Coal | 2289
2023-05-14 04:00 | Western | 8 | HVDC | 918
2023-05-14 05:00 | Eastern | 1 | Gas | 3739
2023-05-14 05:00 | Eastern | 2 | HFO | 979
2023-05-14 05:00 | Eastern | 3 | HSD | 455
2023-05-14 05:00 | Eastern | 10 | Tripura | 134
2023-05-14 05:00 | Western | 1 | Gas | 908
2023-05-14 05:00 | Western | 2 | HFO | 524
2023-05-14 05:00 | Western | 3 | HSD | 0
2023-05-14 05:00 | Western | 6 | Coal | 2288
2023-05-14 05:00 | Western | 8 | HVDC | 918
2023-05-14 06:00 | Eastern | 1 | Gas | 3670
2023-05-14 06:00 | Eastern | 2 | HFO | 966
2023-05-14 06:00 | Eastern | 3 | HSD | 455
2023-05-14 06:00 | Eastern | 10 | Tripura | 130
2023-05-14 06:00 | Eastern | 11 | Solar | 5
2023-05-14 06:00 | Western | 1 | Gas | 906
2023-05-14 06:00 | Western | 2 | HFO | 434
2023-05-14 06:00 | Western | 3 | HSD | 0
2023-05-14 06:00 | Western | 6 | Coal | 2290
2023-05-14 06:00 | Western | 8 | HVDC | 919
2023-05-14 06:00 | Western | 11 | Solar | 19.21
2023-05-14 07:00 | Eastern | 1 | Gas | 3627
2023-05-14 07:00 | Eastern | 2 | HFO | 982
2023-05-14 07:00 | Eastern | 3 | HSD | 455
2023-05-14 07:00 | Eastern | 10 | Tripura | 126
2023-05-14 07:00 | Eastern | 11 | Solar | 12
2023-05-14 07:00 | Western | 1 | Gas | 891
2023-05-14 07:00 | Western | 2 | HFO | 470
2023-05-14 07:00 | Western | 3 | HSD | 0
2023-05-14 07:00 | Western | 6 | Coal | 2287
2023-05-14 07:00 | Western | 8 | HVDC | 919
2023-05-14 07:00 | Western | 11 | Solar | 71.03
2023-05-14 08:00 | Eastern | 1 | Gas | 3646
2023-05-14 08:00 | Eastern | 2 | HFO | 1013
2023-05-14 08:00 | Eastern | 3 | HSD | 311
2023-05-14 08:00 | Eastern | 10 | Tripura | 132
2023-05-14 08:00 | Eastern | 11 | Solar | 22
2023-05-14 08:00 | Western | 1 | Gas | 870
2023-05-14 08:00 | Western | 2 | HFO | 510
2023-05-14 08:00 | Western | 3 | HSD | 0
2023-05-14 08:00 | Western | 6 | Coal | 2074
2023-05-14 08:00 | Western | 8 | HVDC | 921
2023-05-14 08:00 | Western | 11 | Solar | 117.28
2023-05-14 09:00 | Eastern | 1 | Gas | 3596
2023-05-14 09:00 | Eastern | 2 | HFO | 1019
2023-05-14 09:00 | Eastern | 3 | HSD | 405
2023-05-14 09:00 | Eastern | 10 | Tripura | 136
2023-05-14 09:00 | Eastern | 11 | Solar | 37
2023-05-14 09:00 | Western | 1 | Gas | 858
2023-05-14 09:00 | Western | 2 | HFO | 494
2023-05-14 09:00 | Western | 3 | HSD | 0
2023-05-14 09:00 | Western | 6 | Coal | 1972
2023-05-14 09:00 | Western | 8 | HVDC | 921
2023-05-14 09:00 | Western | 11 | Solar | 192.51
2023-05-14 10:00 | Eastern | 1 | Gas | 3400
2023-05-14 10:00 | Eastern | 2 | HFO | 1142
2023-05-14 10:00 | Eastern | 3 | HSD | 454
2023-05-14 10:00 | Eastern | 5 | Hydro | 30
2023-05-14 10:00 | Eastern | 10 | Tripura | 132
2023-05-14 10:00 | Eastern | 11 | Solar | 45
2023-05-14 10:00 | Western | 1 | Gas | 837
2023-05-14 10:00 | Western | 2 | HFO | 511
2023-05-14 10:00 | Western | 3 | HSD | 0
2023-05-14 10:00 | Western | 6 | Coal | 1951
2023-05-14 10:00 | Western | 8 | HVDC | 921
2023-05-14 10:00 | Western | 11 | Solar | 237.15
2023-05-14 11:00 | Eastern | 1 | Gas | 3358
2023-05-14 11:00 | Eastern | 2 | HFO | 1328
2023-05-14 11:00 | Eastern | 3 | HSD | 294
2023-05-14 11:00 | Eastern | 5 | Hydro | 30
2023-05-14 11:00 | Eastern | 10 | Tripura | 136
2023-05-14 11:00 | Eastern | 11 | Solar | 58
2023-05-14 11:00 | Western | 1 | Gas | 830
2023-05-14 11:00 | Western | 2 | HFO | 533
2023-05-14 11:00 | Western | 3 | HSD | 0
2023-05-14 11:00 | Western | 6 | Coal | 1949
2023-05-14 11:00 | Western | 8 | HVDC | 922
2023-05-14 11:00 | Western | 11 | Solar | 290.99
2023-05-14 12:00 | Eastern | 1 | Gas | 3353
2023-05-14 12:00 | Eastern | 2 | HFO | 1380
2023-05-14 12:00 | Eastern | 3 | HSD | 292
2023-05-14 12:00 | Eastern | 5 | Hydro | 30
2023-05-14 12:00 | Eastern | 10 | Tripura | 140
2023-05-14 12:00 | Eastern | 11 | Solar | 57
2023-05-14 12:00 | Western | 1 | Gas | 822
2023-05-14 12:00 | Western | 2 | HFO | 553
2023-05-14 12:00 | Western | 3 | HSD | 0
2023-05-14 12:00 | Western | 6 | Coal | 1927
2023-05-14 12:00 | Western | 8 | HVDC | 921
2023-05-14 12:00 | Western | 11 | Solar | 299.32
2023-05-14 13:00 | Eastern | 1 | Gas | 3348
2023-05-14 13:00 | Eastern | 2 | HFO | 1374
2023-05-14 13:00 | Eastern | 3 | HSD | 428
2023-05-14 13:00 | Eastern | 5 | Hydro | 0
2023-05-14 13:00 | Eastern | 10 | Tripura | 126
2023-05-14 13:00 | Eastern | 11 | Solar | 44
2023-05-14 13:00 | Western | 1 | Gas | 806
2023-05-14 13:00 | Western | 2 | HFO | 587
2023-05-14 13:00 | Western | 3 | HSD | 0
2023-05-14 13:00 | Western | 6 | Coal | 1971
2023-05-14 13:00 | Western | 8 | HVDC | 921
2023-05-14 13:00 | Western | 11 | Solar | 245
2023-05-14 14:00 | Eastern | 1 | Gas | 3085
2023-05-14 14:00 | Eastern | 2 | HFO | 1138
2023-05-14 14:00 | Eastern | 3 | HSD | 270
2023-05-14 14:00 | Eastern | 5 | Hydro | 25
2023-05-14 14:00 | Eastern | 10 | Tripura | 132
2023-05-14 14:00 | Eastern | 11 | Solar | 44
2023-05-14 14:00 | Western | 1 | Gas | 807
2023-05-14 14:00 | Western | 2 | HFO | 585
2023-05-14 14:00 | Western | 3 | HSD | 0
2023-05-14 14:00 | Western | 6 | Coal | 1988
2023-05-14 14:00 | Western | 8 | HVDC | 922
2023-05-14 14:00 | Western | 11 | Solar | 275
2023-05-14 15:00 | Eastern | 1 | Gas | 3008
2023-05-14 15:00 | Eastern | 2 | HFO | 1214
2023-05-14 15:00 | Eastern | 3 | HSD | 455
2023-05-14 15:00 | Eastern | 5 | Hydro | 25
2023-05-14 15:00 | Eastern | 10 | Tripura | 128
2023-05-14 15:00 | Eastern | 11 | Solar | 45
2023-05-14 15:00 | Western | 1 | Gas | 803
2023-05-14 15:00 | Western | 2 | HFO | 550
2023-05-14 15:00 | Western | 3 | HSD | 0
2023-05-14 15:00 | Western | 6 | Coal | 1931
2023-05-14 15:00 | Western | 8 | HVDC | 921
2023-05-14 15:00 | Western | 11 | Solar | 166.36
2023-05-14 16:00 | Eastern | 1 | Gas | 2723
2023-05-14 16:00 | Eastern | 2 | HFO | 1225.5
2023-05-14 16:00 | Eastern | 3 | HSD | 440
2023-05-14 16:00 | Eastern | 5 | Hydro | 25
2023-05-14 16:00 | Eastern | 10 | Tripura | 122
2023-05-14 16:00 | Eastern | 11 | Solar | 29
2023-05-14 16:00 | Western | 1 | Gas | 818
2023-05-14 16:00 | Western | 2 | HFO | 561
2023-05-14 16:00 | Western | 3 | HSD | 0
2023-05-14 16:00 | Western | 6 | Coal | 1926
2023-05-14 16:00 | Western | 8 | HVDC | 922
2023-05-14 16:00 | Western | 11 | Solar | 136.78
2023-05-14 17:00 | Eastern | 1 | Gas | 2710
2023-05-14 17:00 | Eastern | 2 | HFO | 1270
2023-05-14 17:00 | Eastern | 3 | HSD | 417
2023-05-14 17:00 | Eastern | 5 | Hydro | 25
2023-05-14 17:00 | Eastern | 10 | Tripura | 112
2023-05-14 17:00 | Eastern | 11 | Solar | 14
2023-05-14 17:00 | Western | 1 | Gas | 841
2023-05-14 17:00 | Western | 2 | HFO | 557
2023-05-14 17:00 | Western | 3 | HSD | 0
2023-05-14 17:00 | Western | 6 | Coal | 1927
2023-05-14 17:00 | Western | 8 | HVDC | 921
2023-05-14 17:00 | Western | 11 | Solar | 56.14
2023-05-14 18:00 | Eastern | 1 | Gas | 2775
2023-05-14 18:00 | Eastern | 2 | HFO | 1426
2023-05-14 18:00 | Eastern | 3 | HSD | 345
2023-05-14 18:00 | Eastern | 5 | Hydro | 25
2023-05-14 18:00 | Eastern | 10 | Tripura | 112
2023-05-14 18:00 | Eastern | 11 | Solar | 4
2023-05-14 18:00 | Western | 1 | Gas | 853
2023-05-14 18:00 | Western | 2 | HFO | 598
2023-05-14 18:00 | Western | 3 | HSD | 0
2023-05-14 18:00 | Western | 6 | Coal | 1925
2023-05-14 18:00 | Western | 8 | HVDC | 922
2023-05-14 18:00 | Western | 11 | Solar | 18.48
2023-05-14 19:00 | Eastern | 1 | Gas | 2776
2023-05-14 19:00 | Eastern | 2 | HFO | 2079
2023-05-14 19:00 | Eastern | 3 | HSD | 454
2023-05-14 19:00 | Eastern | 5 | Hydro | 25
2023-05-14 19:00 | Eastern | 10 | Tripura | 112
2023-05-14 19:00 | Western | 1 | Gas | 867
2023-05-14 19:00 | Western | 2 | HFO | 838
2023-05-14 19:00 | Western | 3 | HSD | 0
2023-05-14 19:00 | Western | 6 | Coal | 1961
2023-05-14 19:00 | Western | 8 | HVDC | 922
2023-05-14 19:30 | Eastern | 1 | Gas | 2841
2023-05-14 19:30 | Eastern | 2 | HFO | 2268
2023-05-14 19:30 | Eastern | 3 | HSD | 453
2023-05-14 19:30 | Eastern | 5 | Hydro | 25
2023-05-14 19:30 | Eastern | 10 | Tripura | 122
2023-05-14 19:30 | Western | 1 | Gas | 854
2023-05-14 19:30 | Western | 2 | HFO | 976
2023-05-14 19:30 | Western | 3 | HSD | 0
2023-05-14 19:30 | Western | 6 | Coal | 2171
2023-05-14 19:30 | Western | 8 | HVDC | 921
2023-05-14 20:00 | Eastern | 1 | Gas | 2875
2023-05-14 20:00 | Eastern | 2 | HFO | 2267
2023-05-14 20:00 | Eastern | 3 | HSD | 412
2023-05-14 20:00 | Eastern | 5 | Hydro | 25
2023-05-14 20:00 | Eastern | 10 | Tripura | 120
2023-05-14 20:00 | Western | 1 | Gas | 882
2023-05-14 20:00 | Western | 2 | HFO | 1024
2023-05-14 20:00 | Western | 3 | HSD | 0
2023-05-14 20:00 | Western | 6 | Coal | 2221
2023-05-14 20:00 | Western | 8 | HVDC | 921
2023-05-14 21:00 | Eastern | 1 | Gas | 3084.79
2023-05-14 21:00 | Eastern | 2 | HFO | 2281
2023-05-14 21:00 | Eastern | 3 | HSD | 456
2023-05-14 21:00 | Eastern | 5 | Hydro | 25
2023-05-14 21:00 | Eastern | 10 | Tripura | 126
2023-05-14 21:00 | Western | 1 | Gas | 884
2023-05-14 21:00 | Western | 2 | HFO | 1001
2023-05-14 21:00 | Western | 3 | HSD | 0
2023-05-14 21:00 | Western | 6 | Coal | 2293
2023-05-14 21:00 | Western | 8 | HVDC | 875
2023-05-14 22:00 | Eastern | 1 | Gas | 3124.79
2023-05-14 22:00 | Eastern | 2 | HFO | 2177
2023-05-14 22:00 | Eastern | 3 | HSD | 427
2023-05-14 22:00 | Eastern | 5 | Hydro | 25
2023-05-14 22:00 | Eastern | 10 | Tripura | 126
2023-05-14 22:00 | Western | 1 | Gas | 897
2023-05-14 22:00 | Western | 2 | HFO | 898
2023-05-14 22:00 | Western | 3 | HSD | 0
2023-05-14 22:00 | Western | 6 | Coal | 2284
2023-05-14 22:00 | Western | 8 | HVDC | 921
2023-05-14 23:00 | Eastern | 1 | Gas | 3165.79
2023-05-14 23:00 | Eastern | 2 | HFO | 1750
2023-05-14 23:00 | Eastern | 3 | HSD | 428
2023-05-14 23:00 | Eastern | 5 | Hydro | 0
2023-05-14 23:00 | Eastern | 10 | Tripura | 124
2023-05-14 23:00 | Western | 1 | Gas | 912
2023-05-14 23:00 | Western | 2 | HFO | 763
2023-05-14 23:00 | Western | 3 | HSD | 0
2023-05-14 23:00 | Western | 6 | Coal | 2303
2023-05-14 23:00 | Western | 8 | HVDC | 919
2023-05-15 | Eastern | 1 | Gas | 3308
2023-05-15 | Eastern | 2 | HFO | 1223
2023-05-15 | Eastern | 3 | HSD | 418
2023-05-15 | Eastern | 10 | Tripura | 118
2023-05-15 | Eastern | 11 | Solar | 0
2023-05-15 | Western | 1 | Gas | 918
2023-05-15 | Western | 2 | HFO | 636
2023-05-15 | Western | 3 | HSD | 0
2023-05-15 | Western | 6 | Coal | 2299
2023-05-15 | Western | 8 | HVDC | 918
2023-05-15 | Western | 11 | Solar | 0
2023-05-15 01:00 | Eastern | 1 | Gas | 3360.79
2023-05-15 01:00 | Eastern | 2 | HFO | 968
2023-05-15 01:00 | Eastern | 3 | HSD | 418
2023-05-15 01:00 | Eastern | 10 | Tripura | 114
2023-05-15 01:00 | Western | 1 | Gas | 915
2023-05-15 01:00 | Western | 2 | HFO | 512
2023-05-15 01:00 | Western | 3 | HSD | 0
2023-05-15 01:00 | Western | 6 | Coal | 2304
2023-05-15 01:00 | Western | 8 | HVDC | 844
2023-05-15 02:00 | Eastern | 1 | Gas | 3315
2023-05-15 02:00 | Eastern | 2 | HFO | 882
2023-05-15 02:00 | Eastern | 3 | HSD | 419
2023-05-15 02:00 | Eastern | 10 | Tripura | 116
2023-05-15 02:00 | Western | 1 | Gas | 922
2023-05-15 02:00 | Western | 2 | HFO | 470
2023-05-15 02:00 | Western | 3 | HSD | 0
2023-05-15 02:00 | Western | 6 | Coal | 2226
2023-05-15 02:00 | Western | 8 | HVDC | 914
2023-05-15 03:00 | Eastern | 1 | Gas | 3509
2023-05-15 03:00 | Eastern | 2 | HFO | 871
2023-05-15 03:00 | Eastern | 3 | HSD | 358
2023-05-15 03:00 | Eastern | 10 | Tripura | 112
2023-05-15 03:00 | Western | 1 | Gas | 932
2023-05-15 03:00 | Western | 2 | HFO | 359
2023-05-15 03:00 | Western | 3 | HSD | 0
2023-05-15 03:00 | Western | 6 | Coal | 2214
2023-05-15 03:00 | Western | 8 | HVDC | 914
2023-05-15 04:00 | Eastern | 1 | Gas | 3517
2023-05-15 04:00 | Eastern | 2 | HFO | 834
2023-05-15 04:00 | Eastern | 3 | HSD | 362
2023-05-15 04:00 | Eastern | 10 | Tripura | 110
2023-05-15 04:00 | Western | 1 | Gas | 944
2023-05-15 04:00 | Western | 2 | HFO | 357
2023-05-15 04:00 | Western | 3 | HSD | 0
2023-05-15 04:00 | Western | 6 | Coal | 2168
2023-05-15 04:00 | Western | 8 | HVDC | 915
2023-05-15 05:00 | Eastern | 1 | Gas | 3497
2023-05-15 05:00 | Eastern | 2 | HFO | 858
2023-05-15 05:00 | Eastern | 3 | HSD | 359
2023-05-15 05:00 | Eastern | 10 | Tripura | 108
2023-05-15 05:00 | Eastern | 11 | Solar | 0
2023-05-15 05:00 | Western | 1 | Gas | 944
2023-05-15 05:00 | Western | 2 | HFO | 290
2023-05-15 05:00 | Western | 3 | HSD | 0
2023-05-15 05:00 | Western | 6 | Coal | 2161
2023-05-15 05:00 | Western | 8 | HVDC | 914
2023-05-15 05:00 | Western | 11 | Solar | 0
2023-05-15 06:00 | Eastern | 1 | Gas | 3511
2023-05-15 06:00 | Eastern | 2 | HFO | 859
2023-05-15 06:00 | Eastern | 3 | HSD | 288
2023-05-15 06:00 | Eastern | 10 | Tripura | 100
2023-05-15 06:00 | Eastern | 11 | Solar | 5
2023-05-15 06:00 | Western | 1 | Gas | 947
2023-05-15 06:00 | Western | 2 | HFO | 290
2023-05-15 06:00 | Western | 3 | HSD | 0
2023-05-15 06:00 | Western | 6 | Coal | 2012
2023-05-15 06:00 | Western | 8 | HVDC | 914
2023-05-15 06:00 | Western | 11 | Solar | 17.15
2023-05-15 07:00 | Eastern | 1 | Gas | 3517
2023-05-15 07:00 | Eastern | 2 | HFO | 862
2023-05-15 07:00 | Eastern | 3 | HSD | 338
2023-05-15 07:00 | Eastern | 10 | Tripura | 102
2023-05-15 07:00 | Eastern | 11 | Solar | 22
2023-05-15 07:00 | Western | 1 | Gas | 871
2023-05-15 07:00 | Western | 2 | HFO | 355
2023-05-15 07:00 | Western | 3 | HSD | 0
2023-05-15 07:00 | Western | 6 | Coal | 2037
2023-05-15 07:00 | Western | 8 | HVDC | 914
2023-05-15 07:00 | Western | 11 | Solar | 78.44
2023-05-15 08:00 | Eastern | 1 | Gas | 3494
2023-05-15 08:00 | Eastern | 2 | HFO | 907
2023-05-15 08:00 | Eastern | 3 | HSD | 255
2023-05-15 08:00 | Eastern | 10 | Tripura | 104
2023-05-15 08:00 | Eastern | 11 | Solar | 54
2023-05-15 08:00 | Western | 1 | Gas | 930
2023-05-15 08:00 | Western | 2 | HFO | 402
2023-05-15 08:00 | Western | 3 | HSD | 0
2023-05-15 08:00 | Western | 6 | Coal | 2044
2023-05-15 08:00 | Western | 8 | HVDC | 913
2023-05-15 08:00 | Western | 11 | Solar | 101.22
2023-05-15 09:00 | Eastern | 1 | Gas | 3462
2023-05-15 09:00 | Eastern | 2 | HFO | 930
2023-05-15 09:00 | Eastern | 3 | HSD | 246
2023-05-15 09:00 | Eastern | 10 | Tripura | 120
2023-05-15 09:00 | Eastern | 11 | Solar | 67
2023-05-15 09:00 | Western | 1 | Gas | 903
2023-05-15 09:00 | Western | 2 | HFO | 394
2023-05-15 09:00 | Western | 3 | HSD | 0
2023-05-15 09:00 | Western | 6 | Coal | 2033
2023-05-15 09:00 | Western | 8 | HVDC | 914
2023-05-15 09:00 | Western | 11 | Solar | 177.64
2023-05-15 10:00 | Eastern | 1 | Gas | 3399
2023-05-15 10:00 | Eastern | 2 | HFO | 1169
2023-05-15 10:00 | Eastern | 3 | HSD | 311
2023-05-15 10:00 | Eastern | 10 | Tripura | 138
2023-05-15 10:00 | Eastern | 11 | Solar | 82
2023-05-15 10:00 | Western | 1 | Gas | 890
2023-05-15 10:00 | Western | 2 | HFO | 406
2023-05-15 10:00 | Western | 3 | HSD | 0
2023-05-15 10:00 | Western | 6 | Coal | 1970
2023-05-15 10:00 | Western | 8 | HVDC | 914
2023-05-15 10:00 | Western | 11 | Solar | 269.54
2023-05-15 11:00 | Eastern | 1 | Gas | 3416
2023-05-15 11:00 | Eastern | 2 | HFO | 1273
2023-05-15 11:00 | Eastern | 3 | HSD | 428
2023-05-15 11:00 | Eastern | 5 | Hydro | 0
2023-05-15 11:00 | Eastern | 10 | Tripura | 148
2023-05-15 11:00 | Eastern | 11 | Solar | 110
2023-05-15 11:00 | Western | 1 | Gas | 860
2023-05-15 11:00 | Western | 2 | HFO | 452
2023-05-15 11:00 | Western | 3 | HSD | 0
2023-05-15 11:00 | Western | 6 | Coal | 1955
2023-05-15 11:00 | Western | 8 | HVDC | 913
2023-05-15 11:00 | Western | 11 | Solar | 305.01
2023-05-15 12:00 | Eastern | 1 | Gas | 3372
2023-05-15 12:00 | Eastern | 2 | HFO | 1422
2023-05-15 12:00 | Eastern | 3 | HSD | 430
2023-05-15 12:00 | Eastern | 5 | Hydro | 27
2023-05-15 12:00 | Eastern | 10 | Tripura | 152
2023-05-15 12:00 | Eastern | 11 | Solar | 102
2023-05-15 12:00 | Western | 1 | Gas | 828
2023-05-15 12:00 | Western | 2 | HFO | 472
2023-05-15 12:00 | Western | 3 | HSD | 0
2023-05-15 12:00 | Western | 6 | Coal | 1963
2023-05-15 12:00 | Western | 8 | HVDC | 913
2023-05-15 12:00 | Western | 11 | Solar | 303.29
2023-05-15 13:00 | Eastern | 1 | Gas | 3393
2023-05-15 13:00 | Eastern | 2 | HFO | 1456
2023-05-15 13:00 | Eastern | 3 | HSD | 430
2023-05-15 13:00 | Eastern | 5 | Hydro | 27
2023-05-15 13:00 | Eastern | 10 | Tripura | 156
2023-05-15 13:00 | Eastern | 11 | Solar | 100
2023-05-15 13:00 | Western | 1 | Gas | 831
2023-05-15 13:00 | Western | 2 | HFO | 495
2023-05-15 13:00 | Western | 3 | HSD | 0
2023-05-15 13:00 | Western | 6 | Coal | 2090
2023-05-15 13:00 | Western | 8 | HVDC | 913
2023-05-15 13:00 | Western | 11 | Solar | 220.07
2023-05-15 14:00 | Eastern | 1 | Gas | 3435
2023-05-15 14:00 | Eastern | 2 | HFO | 1385
2023-05-15 14:00 | Eastern | 3 | HSD | 337
2023-05-15 14:00 | Eastern | 5 | Hydro | 27
2023-05-15 14:00 | Eastern | 10 | Tripura | 170
2023-05-15 14:00 | Eastern | 11 | Solar | 86
2023-05-15 14:00 | Western | 1 | Gas | 833
2023-05-15 14:00 | Western | 2 | HFO | 538
2023-05-15 14:00 | Western | 3 | HSD | 0
2023-05-15 14:00 | Western | 6 | Coal | 2189
2023-05-15 14:00 | Western | 8 | HVDC | 914
2023-05-15 14:00 | Western | 11 | Solar | 176.34
2023-05-15 15:00 | Eastern | 1 | Gas | 3413
2023-05-15 15:00 | Eastern | 2 | HFO | 1339
2023-05-15 15:00 | Eastern | 3 | HSD | 430
2023-05-15 15:00 | Eastern | 5 | Hydro | 25
2023-05-15 15:00 | Eastern | 10 | Tripura | 176
2023-05-15 15:00 | Eastern | 11 | Solar | 59
2023-05-15 15:00 | Western | 1 | Gas | 829
2023-05-15 15:00 | Western | 2 | HFO | 540
2023-05-15 15:00 | Western | 3 | HSD | 0
2023-05-15 15:00 | Western | 6 | Coal | 2226
2023-05-15 15:00 | Western | 8 | HVDC | 913
2023-05-15 15:00 | Western | 11 | Solar | 119.27
2023-05-15 16:00 | Eastern | 1 | Gas | 3430
2023-05-15 16:00 | Eastern | 2 | HFO | 1407
2023-05-15 16:00 | Eastern | 3 | HSD | 422
2023-05-15 16:00 | Eastern | 5 | Hydro | 25
2023-05-15 16:00 | Eastern | 10 | Tripura | 166
2023-05-15 16:00 | Eastern | 11 | Solar | 43
2023-05-15 16:00 | Western | 1 | Gas | 830
2023-05-15 16:00 | Western | 2 | HFO | 522
2023-05-15 16:00 | Western | 3 | HSD | 0
2023-05-15 16:00 | Western | 6 | Coal | 2270
2023-05-15 16:00 | Western | 8 | HVDC | 914
2023-05-15 16:00 | Western | 11 | Solar | 100.03
2023-05-15 17:00 | Eastern | 1 | Gas | 3417
2023-05-15 17:00 | Eastern | 2 | HFO | 1495
2023-05-15 17:00 | Eastern | 3 | HSD | 407
2023-05-15 17:00 | Eastern | 5 | Hydro | 25
2023-05-15 17:00 | Eastern | 10 | Tripura | 160
2023-05-15 17:00 | Eastern | 11 | Solar | 14
2023-05-15 17:00 | Western | 1 | Gas | 838
2023-05-15 17:00 | Western | 2 | HFO | 534
2023-05-15 17:00 | Western | 3 | HSD | 0
2023-05-15 17:00 | Western | 6 | Coal | 2283
2023-05-15 17:00 | Western | 8 | HVDC | 913
2023-05-15 17:00 | Western | 11 | Solar | 52.92
2023-05-15 18:00 | Eastern | 1 | Gas | 3407
2023-05-15 18:00 | Eastern | 2 | HFO | 1771
2023-05-15 18:00 | Eastern | 3 | HSD | 280
2023-05-15 18:00 | Eastern | 5 | Hydro | 25
2023-05-15 18:00 | Eastern | 10 | Tripura | 152
2023-05-15 18:00 | Eastern | 11 | Solar | 3
2023-05-15 18:00 | Western | 1 | Gas | 826
2023-05-15 18:00 | Western | 2 | HFO | 580
2023-05-15 18:00 | Western | 3 | HSD | 0
2023-05-15 18:00 | Western | 6 | Coal | 2215
2023-05-15 18:00 | Western | 8 | HVDC | 914
2023-05-15 18:00 | Western | 11 | Solar | 9.18
2023-05-15 19:00 | Eastern | 1 | Gas | 3378
2023-05-15 19:00 | Eastern | 2 | HFO | 2395
2023-05-15 19:00 | Eastern | 3 | HSD | 448
2023-05-15 19:00 | Eastern | 5 | Hydro | 25
2023-05-15 19:00 | Eastern | 10 | Tripura | 172
2023-05-15 19:00 | Western | 1 | Gas | 805
2023-05-15 19:00 | Western | 2 | HFO | 857
2023-05-15 19:00 | Western | 3 | HSD | 0
2023-05-15 19:00 | Western | 6 | Coal | 2235
2023-05-15 19:00 | Western | 8 | HVDC | 913
2023-05-15 19:30 | Eastern | 1 | Gas | 3396
2023-05-15 19:30 | Eastern | 2 | HFO | 2631
2023-05-15 19:30 | Eastern | 3 | HSD | 375
2023-05-15 19:30 | Eastern | 5 | Hydro | 25
2023-05-15 19:30 | Eastern | 10 | Tripura | 160
2023-05-15 19:30 | Western | 1 | Gas | 790
2023-05-15 19:30 | Western | 2 | HFO | 952
2023-05-15 19:30 | Western | 3 | HSD | 0
2023-05-15 19:30 | Western | 6 | Coal | 2260
2023-05-15 19:30 | Western | 8 | HVDC | 853
2023-05-15 20:00 | Eastern | 1 | Gas | 3485
2023-05-15 20:00 | Eastern | 2 | HFO | 2674
2023-05-15 20:00 | Eastern | 3 | HSD | 473
2023-05-15 20:00 | Eastern | 5 | Hydro | 25
2023-05-15 20:00 | Eastern | 10 | Tripura | 162
2023-05-15 20:00 | Western | 1 | Gas | 878
2023-05-15 20:00 | Western | 2 | HFO | 852
2023-05-15 20:00 | Western | 3 | HSD | 0
2023-05-15 20:00 | Western | 6 | Coal | 2094
2023-05-15 20:00 | Western | 8 | HVDC | 853
2023-05-15 21:00 | Eastern | 1 | Gas | 3518
2023-05-15 21:00 | Eastern | 2 | HFO | 2708
2023-05-15 21:00 | Eastern | 3 | HSD | 549
2023-05-15 21:00 | Eastern | 5 | Hydro | 25
2023-05-15 21:00 | Eastern | 10 | Tripura | 174
2023-05-15 21:00 | Western | 1 | Gas | 891
2023-05-15 21:00 | Western | 2 | HFO | 653
2023-05-15 21:00 | Western | 3 | HSD | 0
2023-05-15 21:00 | Western | 6 | Coal | 1837
2023-05-15 21:00 | Western | 8 | HVDC | 818
2023-05-15 22:00 | Eastern | 1 | Gas | 3517
2023-05-15 22:00 | Eastern | 2 | HFO | 2499
2023-05-15 22:00 | Eastern | 3 | HSD | 608
2023-05-15 22:00 | Eastern | 5 | Hydro | 25
2023-05-15 22:00 | Eastern | 10 | Tripura | 166
2023-05-15 22:00 | Western | 1 | Gas | 791
2023-05-15 22:00 | Western | 2 | HFO | 631
2023-05-15 22:00 | Western | 3 | HSD | 0
2023-05-15 22:00 | Western | 6 | Coal | 1806
2023-05-15 22:00 | Western | 8 | HVDC | 819
2023-05-15 23:00 | Eastern | 1 | Gas | 3472
2023-05-15 23:00 | Eastern | 2 | HFO | 1964
2023-05-15 23:00 | Eastern | 3 | HSD | 555
2023-05-15 23:00 | Eastern | 5 | Hydro | 25
2023-05-15 23:00 | Eastern | 10 | Tripura | 135
2023-05-15 23:00 | Western | 1 | Gas | 803
2023-05-15 23:00 | Western | 2 | HFO | 545
2023-05-15 23:00 | Western | 3 | HSD | 0
2023-05-15 23:00 | Western | 6 | Coal | 1884
2023-05-15 23:00 | Western | 8 | HVDC | 818
2023-05-16 | Eastern | 1 | Gas | 3503
2023-05-16 | Eastern | 2 | HFO | 1137
2023-05-16 | Eastern | 3 | HSD | 489
2023-05-16 | Eastern | 5 | Hydro | 0
2023-05-16 | Eastern | 10 | Tripura | 146
2023-05-16 | Western | 1 | Gas | 809
2023-05-16 | Western | 2 | HFO | 457
2023-05-16 | Western | 6 | Coal | 1990
2023-05-16 | Western | 8 | HVDC | 819
2023-05-16 01:00 | Eastern | 1 | Gas | 3527
2023-05-16 01:00 | Eastern | 2 | HFO | 905
2023-05-16 01:00 | Eastern | 3 | HSD | 459
2023-05-16 01:00 | Eastern | 10 | Tripura | 160
2023-05-16 01:00 | Western | 1 | Gas | 816
2023-05-16 01:00 | Western | 2 | HFO | 470
2023-05-16 01:00 | Western | 6 | Coal | 2068
2023-05-16 01:00 | Western | 8 | HVDC | 819
2023-05-16 02:00 | Eastern | 1 | Gas | 3569
2023-05-16 02:00 | Eastern | 2 | HFO | 870
2023-05-16 02:00 | Eastern | 3 | HSD | 585
2023-05-16 02:00 | Eastern | 10 | Tripura | 160
2023-05-16 02:00 | Western | 1 | Gas | 828
2023-05-16 02:00 | Western | 2 | HFO | 481
2023-05-16 02:00 | Western | 6 | Coal | 2078
2023-05-16 02:00 | Western | 8 | HVDC | 787
2023-05-16 03:00 | Eastern | 1 | Gas | 3556
2023-05-16 03:00 | Eastern | 2 | HFO | 892
2023-05-16 03:00 | Eastern | 3 | HSD | 580
2023-05-16 03:00 | Eastern | 10 | Tripura | 154
2023-05-16 03:00 | Western | 1 | Gas | 829
2023-05-16 03:00 | Western | 2 | HFO | 378
2023-05-16 03:00 | Western | 6 | Coal | 2199
2023-05-16 03:00 | Western | 8 | HVDC | 630
2023-05-16 04:00 | Eastern | 1 | Gas | 3548
2023-05-16 04:00 | Eastern | 2 | HFO | 882
2023-05-16 04:00 | Eastern | 3 | HSD | 537
2023-05-16 04:00 | Eastern | 10 | Tripura | 150
2023-05-16 04:00 | Western | 1 | Gas | 829
2023-05-16 04:00 | Western | 2 | HFO | 345
2023-05-16 04:00 | Western | 6 | Coal | 2205
2023-05-16 04:00 | Western | 8 | HVDC | 630
2023-05-16 05:00 | Eastern | 1 | Gas | 3562
2023-05-16 05:00 | Eastern | 2 | HFO | 918
2023-05-16 05:00 | Eastern | 3 | HSD | 487
2023-05-16 05:00 | Eastern | 10 | Tripura | 140
2023-05-16 05:00 | Western | 1 | Gas | 842
2023-05-16 05:00 | Western | 2 | HFO | 295
2023-05-16 05:00 | Western | 6 | Coal | 2178
2023-05-16 05:00 | Western | 8 | HVDC | 630
2023-05-16 06:00 | Eastern | 1 | Gas | 3516
2023-05-16 06:00 | Eastern | 2 | HFO | 902
2023-05-16 06:00 | Eastern | 3 | HSD | 456
2023-05-16 06:00 | Eastern | 10 | Tripura | 124
2023-05-16 06:00 | Eastern | 11 | Solar | 5
2023-05-16 06:00 | Western | 1 | Gas | 844
2023-05-16 06:00 | Western | 2 | HFO | 209
2023-05-16 06:00 | Western | 6 | Coal | 2138
2023-05-16 06:00 | Western | 8 | HVDC | 630
2023-05-16 06:00 | Western | 11 | Solar | 19.29
2023-05-16 07:00 | Eastern | 1 | Gas | 3381
2023-05-16 07:00 | Eastern | 2 | HFO | 905
2023-05-16 07:00 | Eastern | 3 | HSD | 585
2023-05-16 07:00 | Eastern | 10 | Tripura | 124
2023-05-16 07:00 | Eastern | 11 | Solar | 22
2023-05-16 07:00 | Western | 1 | Gas | 830
2023-05-16 07:00 | Western | 2 | HFO | 271
2023-05-16 07:00 | Western | 6 | Coal | 2148
2023-05-16 07:00 | Western | 8 | HVDC | 627
2023-05-16 07:00 | Western | 11 | Solar | 75.95
2023-05-16 08:00 | Eastern | 1 | Gas | 3431
2023-05-16 08:00 | Eastern | 2 | HFO | 907
2023-05-16 08:00 | Eastern | 3 | HSD | 578
2023-05-16 08:00 | Eastern | 10 | Tripura | 138
2023-05-16 08:00 | Eastern | 11 | Solar | 51
2023-05-16 08:00 | Western | 1 | Gas | 805
2023-05-16 08:00 | Western | 2 | HFO | 314
2023-05-16 08:00 | Western | 6 | Coal | 2224
2023-05-16 08:00 | Western | 8 | HVDC | 627
2023-05-16 08:00 | Western | 11 | Solar | 161.24
2023-05-16 09:00 | Eastern | 1 | Gas | 3452
2023-05-16 09:00 | Eastern | 2 | HFO | 936
2023-05-16 09:00 | Eastern | 3 | HSD | 435
2023-05-16 09:00 | Eastern | 10 | Tripura | 142
2023-05-16 09:00 | Eastern | 11 | Solar | 81
2023-05-16 09:00 | Western | 1 | Gas | 780
2023-05-16 09:00 | Western | 2 | HFO | 327
2023-05-16 09:00 | Western | 6 | Coal | 2113
2023-05-16 09:00 | Western | 8 | HVDC | 627
2023-05-16 09:00 | Western | 11 | Solar | 223.38
2023-05-16 10:00 | Eastern | 1 | Gas | 3438
2023-05-16 10:00 | Eastern | 2 | HFO | 1246
2023-05-16 10:00 | Eastern | 3 | HSD | 572
2023-05-16 10:00 | Eastern | 5 | Hydro | 0
2023-05-16 10:00 | Eastern | 10 | Tripura | 150
2023-05-16 10:00 | Eastern | 11 | Solar | 100
2023-05-16 10:00 | Western | 1 | Gas | 750
2023-05-16 10:00 | Western | 2 | HFO | 355
2023-05-16 10:00 | Western | 6 | Coal | 2163
2023-05-16 10:00 | Western | 8 | HVDC | 627
2023-05-16 10:00 | Western | 11 | Solar | 247.23
2023-05-16 11:00 | Eastern | 1 | Gas | 3439
2023-05-16 11:00 | Eastern | 2 | HFO | 1369
2023-05-16 11:00 | Eastern | 3 | HSD | 535
2023-05-16 11:00 | Eastern | 5 | Hydro | 27
2023-05-16 11:00 | Eastern | 10 | Tripura | 156
2023-05-16 11:00 | Eastern | 11 | Solar | 106
2023-05-16 11:00 | Western | 1 | Gas | 756
2023-05-16 11:00 | Western | 2 | HFO | 488
2023-05-16 11:00 | Western | 6 | Coal | 2213
2023-05-16 11:00 | Western | 8 | HVDC | 633
2023-05-16 11:00 | Western | 11 | Solar | 228.78
2023-05-16 12:00 | Eastern | 1 | Gas | 3422
2023-05-16 12:00 | Eastern | 2 | HFO | 1482
2023-05-16 12:00 | Eastern | 3 | HSD | 575
2023-05-16 12:00 | Eastern | 5 | Hydro | 27
2023-05-16 12:00 | Eastern | 10 | Tripura | 166
2023-05-16 12:00 | Eastern | 11 | Solar | 109
2023-05-16 12:00 | Western | 1 | Gas | 733
2023-05-16 12:00 | Western | 2 | HFO | 535
2023-05-16 12:00 | Western | 3 | HSD | 0
2023-05-16 12:00 | Western | 6 | Coal | 2281
2023-05-16 12:00 | Western | 8 | HVDC | 633
2023-05-16 12:00 | Western | 11 | Solar | 181
2023-05-16 13:00 | Eastern | 1 | Gas | 3403
2023-05-16 13:00 | Eastern | 2 | HFO | 1513
2023-05-16 13:00 | Eastern | 3 | HSD | 386
2023-05-16 13:00 | Eastern | 5 | Hydro | 27
2023-05-16 13:00 | Eastern | 10 | Tripura | 156
2023-05-16 13:00 | Eastern | 11 | Solar | 67
2023-05-16 13:00 | Western | 1 | Gas | 725
2023-05-16 13:00 | Western | 2 | HFO | 572
2023-05-16 13:00 | Western | 3 | HSD | 18
2023-05-16 13:00 | Western | 6 | Coal | 2369
2023-05-16 13:00 | Western | 8 | HVDC | 632
2023-05-16 13:00 | Western | 11 | Solar | 275.84
2023-05-16 14:00 | Eastern | 1 | Gas | 3419
2023-05-16 14:00 | Eastern | 2 | HFO | 1407
2023-05-16 14:00 | Eastern | 3 | HSD | 426
2023-05-16 14:00 | Eastern | 5 | Hydro | 27
2023-05-16 14:00 | Eastern | 10 | Tripura | 170
2023-05-16 14:00 | Eastern | 11 | Solar | 89
2023-05-16 14:00 | Western | 1 | Gas | 727
2023-05-16 14:00 | Western | 2 | HFO | 588
2023-05-16 14:00 | Western | 3 | HSD | 20
2023-05-16 14:00 | Western | 6 | Coal | 2354
2023-05-16 14:00 | Western | 8 | HVDC | 628
2023-05-16 14:00 | Western | 11 | Solar | 260.59
2023-05-16 15:00 | Eastern | 1 | Gas | 3336
2023-05-16 15:00 | Eastern | 2 | HFO | 1369
2023-05-16 15:00 | Eastern | 3 | HSD | 572
2023-05-16 15:00 | Eastern | 5 | Hydro | 27
2023-05-16 15:00 | Eastern | 10 | Tripura | 166
2023-05-16 15:00 | Eastern | 11 | Solar | 57
2023-05-16 15:00 | Western | 1 | Gas | 745
2023-05-16 15:00 | Western | 2 | HFO | 603
2023-05-16 15:00 | Western | 3 | HSD | 40
2023-05-16 15:00 | Western | 6 | Coal | 2350
2023-05-16 15:00 | Western | 8 | HVDC | 627
2023-05-16 15:00 | Western | 11 | Solar | 209.52
2023-05-16 16:00 | Eastern | 1 | Gas | 3400
2023-05-16 16:00 | Eastern | 2 | HFO | 1398
2023-05-16 16:00 | Eastern | 3 | HSD | 496
2023-05-16 16:00 | Eastern | 5 | Hydro | 27
2023-05-16 16:00 | Eastern | 10 | Tripura | 164
2023-05-16 16:00 | Eastern | 11 | Solar | 31
2023-05-16 16:00 | Western | 1 | Gas | 758
2023-05-16 16:00 | Western | 2 | HFO | 637
2023-05-16 16:00 | Western | 3 | HSD | 20
2023-05-16 16:00 | Western | 6 | Coal | 2331
2023-05-16 16:00 | Western | 8 | HVDC | 627
2023-05-16 16:00 | Western | 11 | Solar | 143.06
2023-05-16 17:00 | Eastern | 1 | Gas | 3490
2023-05-16 17:00 | Eastern | 2 | HFO | 1457
2023-05-16 17:00 | Eastern | 3 | HSD | 363
2023-05-16 17:00 | Eastern | 5 | Hydro | 27
2023-05-16 17:00 | Eastern | 10 | Tripura | 158
2023-05-16 17:00 | Eastern | 11 | Solar | 18
2023-05-16 17:00 | Western | 1 | Gas | 748
2023-05-16 17:00 | Western | 2 | HFO | 651
2023-05-16 17:00 | Western | 3 | HSD | 40
2023-05-16 17:00 | Western | 6 | Coal | 2312
2023-05-16 17:00 | Western | 8 | HVDC | 628
2023-05-16 17:00 | Western | 11 | Solar | 61.45
2023-05-16 18:00 | Eastern | 1 | Gas | 3327
2023-05-16 18:00 | Eastern | 2 | HFO | 1683
2023-05-16 18:00 | Eastern | 3 | HSD | 148
2023-05-16 18:00 | Eastern | 5 | Hydro | 27
2023-05-16 18:00 | Eastern | 10 | Tripura | 152
2023-05-16 18:00 | Eastern | 11 | Solar | 0
2023-05-16 18:00 | Western | 1 | Gas | 822
2023-05-16 18:00 | Western | 2 | HFO | 646
2023-05-16 18:00 | Western | 3 | HSD | 40
2023-05-16 18:00 | Western | 6 | Coal | 2082
2023-05-16 18:00 | Western | 8 | HVDC | 911
2023-05-16 18:00 | Western | 11 | Solar | 14.07
2023-05-16 19:00 | Eastern | 1 | Gas | 3340
2023-05-16 19:00 | Eastern | 2 | HFO | 2448
2023-05-16 19:00 | Eastern | 3 | HSD | 300
2023-05-16 19:00 | Eastern | 5 | Hydro | 27
2023-05-16 19:00 | Eastern | 10 | Tripura | 166
2023-05-16 19:00 | Western | 1 | Gas | 851
2023-05-16 19:00 | Western | 2 | HFO | 962
2023-05-16 19:00 | Western | 3 | HSD | 40
2023-05-16 19:00 | Western | 6 | Coal | 2037
2023-05-16 19:00 | Western | 8 | HVDC | 911
2023-05-16 19:00 | Western | 11 | Solar | 0
2023-05-16 19:30 | Eastern | 1 | Gas | 3445
2023-05-16 19:30 | Eastern | 2 | HFO | 2604
2023-05-16 19:30 | Eastern | 3 | HSD | 297
2023-05-16 19:30 | Eastern | 5 | Hydro | 27
2023-05-16 19:30 | Eastern | 10 | Tripura | 164
2023-05-16 19:30 | Western | 1 | Gas | 745
2023-05-16 19:30 | Western | 2 | HFO | 738
2023-05-16 19:30 | Western | 3 | HSD | 0
2023-05-16 19:30 | Western | 6 | Coal | 1846
2023-05-16 19:30 | Western | 8 | HVDC | 911
2023-05-16 20:00 | Eastern | 1 | Gas | 3056
2023-05-16 20:00 | Eastern | 2 | HFO | 2067
2023-05-16 20:00 | Eastern | 3 | HSD | 148
2023-05-16 20:00 | Eastern | 5 | Hydro | 27
2023-05-16 20:00 | Eastern | 10 | Tripura | 162
2023-05-16 20:00 | Western | 1 | Gas | 673
2023-05-16 20:00 | Western | 2 | HFO | 357
2023-05-16 20:00 | Western | 6 | Coal | 1519
2023-05-16 20:00 | Western | 8 | HVDC | 453
2023-05-16 21:00 | Eastern | 1 | Gas | 3337
2023-05-16 21:00 | Eastern | 2 | HFO | 1092
2023-05-16 21:00 | Eastern | 3 | HSD | 146
2023-05-16 21:00 | Eastern | 5 | Hydro | 27
2023-05-16 21:00 | Eastern | 10 | Tripura | 32
2023-05-16 21:00 | Western | 1 | Gas | 748
2023-05-16 21:00 | Western | 2 | HFO | 0
2023-05-16 21:00 | Western | 6 | Coal | 1476
2023-05-16 21:00 | Western | 8 | HVDC | 912
2023-05-16 22:00 | Eastern | 1 | Gas | 3540
2023-05-16 22:00 | Eastern | 2 | HFO | 933
2023-05-16 22:00 | Eastern | 3 | HSD | 146
2023-05-16 22:00 | Eastern | 5 | Hydro | 27
2023-05-16 22:00 | Eastern | 10 | Tripura | 108
2023-05-16 22:00 | Western | 1 | Gas | 811
2023-05-16 22:00 | Western | 6 | Coal | 1744
2023-05-16 22:00 | Western | 8 | HVDC | 912
2023-05-16 23:00 | Eastern | 1 | Gas | 3672
2023-05-16 23:00 | Eastern | 2 | HFO | 1100
2023-05-16 23:00 | Eastern | 3 | HSD | 250
2023-05-16 23:00 | Eastern | 5 | Hydro | 0
2023-05-16 23:00 | Eastern | 10 | Tripura | 138
2023-05-16 23:00 | Western | 1 | Gas | 952
2023-05-16 23:00 | Western | 2 | HFO | 56
2023-05-16 23:00 | Western | 6 | Coal | 1865
2023-05-16 23:00 | Western | 8 | HVDC | 912
2023-05-17 | Eastern | 1 | Gas | 3735
2023-05-17 | Eastern | 2 | HFO | 1279
2023-05-17 | Eastern | 3 | HSD | 320
2023-05-17 | Eastern | 10 | Tripura | 134
2023-05-17 | Eastern | 11 | Solar | 0
2023-05-17 | Western | 1 | Gas | 965
2023-05-17 | Western | 2 | HFO | 157
2023-05-17 | Western | 6 | Coal | 1990
2023-05-17 | Western | 8 | HVDC | 911
2023-05-17 01:00 | Eastern | 1 | Gas | 3993
2023-05-17 01:00 | Eastern | 2 | HFO | 1049
2023-05-17 01:00 | Eastern | 3 | HSD | 485
2023-05-17 01:00 | Eastern | 10 | Tripura | 130
2023-05-17 01:00 | Western | 1 | Gas | 966
2023-05-17 01:00 | Western | 2 | HFO | 153
2023-05-17 01:00 | Western | 6 | Coal | 2095
2023-05-17 01:00 | Western | 8 | HVDC | 816
2023-05-17 02:00 | Eastern | 1 | Gas | 3935.5
2023-05-17 02:00 | Eastern | 2 | HFO | 1009
2023-05-17 02:00 | Eastern | 3 | HSD | 359
2023-05-17 02:00 | Eastern | 10 | Tripura | 130
2023-05-17 02:00 | Western | 1 | Gas | 977
2023-05-17 02:00 | Western | 2 | HFO | 247
2023-05-17 02:00 | Western | 6 | Coal | 2080
2023-05-17 02:00 | Western | 8 | HVDC | 853
2023-05-17 03:00 | Eastern | 1 | Gas | 3967.5
2023-05-17 03:00 | Eastern | 2 | HFO | 1014
2023-05-17 03:00 | Eastern | 3 | HSD | 172
2023-05-17 03:00 | Eastern | 10 | Tripura | 128
2023-05-17 03:00 | Western | 1 | Gas | 977
2023-05-17 03:00 | Western | 2 | HFO | 240
2023-05-17 03:00 | Western | 6 | Coal | 2036
2023-05-17 03:00 | Western | 8 | HVDC | 911
2023-05-17 04:00 | Eastern | 1 | Gas | 4003.5
2023-05-17 04:00 | Eastern | 2 | HFO | 781
2023-05-17 04:00 | Eastern | 3 | HSD | 151
2023-05-17 04:00 | Eastern | 10 | Tripura | 124
2023-05-17 04:00 | Western | 1 | Gas | 958
2023-05-17 04:00 | Western | 2 | HFO | 151
2023-05-17 04:00 | Western | 6 | Coal | 1936
2023-05-17 04:00 | Western | 8 | HVDC | 911
2023-05-17 05:00 | Eastern | 1 | Gas | 4012.5
2023-05-17 05:00 | Eastern | 2 | HFO | 670
2023-05-17 05:00 | Eastern | 3 | HSD | 80
2023-05-17 05:00 | Eastern | 10 | Tripura | 116
2023-05-17 05:00 | Western | 1 | Gas | 820
2023-05-17 05:00 | Western | 2 | HFO | 137
2023-05-17 05:00 | Western | 6 | Coal | 1843
2023-05-17 05:00 | Western | 8 | HVDC | 910
2023-05-17 06:00 | Eastern | 1 | Gas | 3958.5
2023-05-17 06:00 | Eastern | 2 | HFO | 648
2023-05-17 06:00 | Eastern | 3 | HSD | 61
2023-05-17 06:00 | Eastern | 10 | Tripura | 110
2023-05-17 06:00 | Eastern | 11 | Solar | 7
2023-05-17 06:00 | Western | 1 | Gas | 859
2023-05-17 06:00 | Western | 2 | HFO | 137
2023-05-17 06:00 | Western | 6 | Coal | 1788
2023-05-17 06:00 | Western | 8 | HVDC | 911
2023-05-17 06:00 | Western | 11 | Solar | 2.11
2023-05-17 07:00 | Eastern | 1 | Gas | 3832.5
2023-05-17 07:00 | Eastern | 2 | HFO | 639
2023-05-17 07:00 | Eastern | 3 | HSD | 31
2023-05-17 07:00 | Eastern | 10 | Tripura | 110
2023-05-17 07:00 | Eastern | 11 | Solar | 9
2023-05-17 07:00 | Western | 1 | Gas | 910
2023-05-17 07:00 | Western | 2 | HFO | 193
2023-05-17 07:00 | Western | 3 | HSD | 25
2023-05-17 07:00 | Western | 6 | Coal | 1784
2023-05-17 07:00 | Western | 8 | HVDC | 911
2023-05-17 07:00 | Western | 11 | Solar | 28.25
2023-05-17 08:00 | Eastern | 1 | Gas | 3815
2023-05-17 08:00 | Eastern | 2 | HFO | 630
2023-05-17 08:00 | Eastern | 3 | HSD | 31
2023-05-17 08:00 | Eastern | 10 | Tripura | 126
2023-05-17 08:00 | Eastern | 11 | Solar | 17
2023-05-17 08:00 | Western | 1 | Gas | 916
2023-05-17 08:00 | Western | 2 | HFO | 248
2023-05-17 08:00 | Western | 3 | HSD | 22
2023-05-17 08:00 | Western | 6 | Coal | 1783
2023-05-17 08:00 | Western | 8 | HVDC | 911
2023-05-17 08:00 | Western | 11 | Solar | 109
2023-05-17 09:00 | Eastern | 1 | Gas | 3754
2023-05-17 09:00 | Eastern | 2 | HFO | 725
2023-05-17 09:00 | Eastern | 3 | HSD | 31
2023-05-17 09:00 | Eastern | 10 | Tripura | 122
2023-05-17 09:00 | Eastern | 11 | Solar | 21
2023-05-17 09:00 | Western | 1 | Gas | 792
2023-05-17 09:00 | Western | 2 | HFO | 109
2023-05-17 09:00 | Western | 3 | HSD | 69
2023-05-17 09:00 | Western | 6 | Coal | 1761
2023-05-17 09:00 | Western | 8 | HVDC | 911
2023-05-17 09:00 | Western | 11 | Solar | 174.88
2023-05-17 10:00 | Eastern | 1 | Gas | 3129
2023-05-17 10:00 | Eastern | 2 | HFO | 592
2023-05-17 10:00 | Eastern | 3 | HSD | 76
2023-05-17 10:00 | Eastern | 10 | Tripura | 136
2023-05-17 10:00 | Eastern | 11 | Solar | 55
2023-05-17 10:00 | Western | 1 | Gas | 765
2023-05-17 10:00 | Western | 3 | HSD | 114
2023-05-17 10:00 | Western | 6 | Coal | 1749
2023-05-17 10:00 | Western | 8 | HVDC | 910
2023-05-17 10:00 | Western | 11 | Solar | 198.93
2023-05-17 11:00 | Eastern | 1 | Gas | 3617
2023-05-17 11:00 | Eastern | 2 | HFO | 880
2023-05-17 11:00 | Eastern | 3 | HSD | 50
2023-05-17 11:00 | Eastern | 5 | Hydro | 25
2023-05-17 11:00 | Eastern | 10 | Tripura | 54
2023-05-17 11:00 | Eastern | 11 | Solar | 50
2023-05-17 11:00 | Western | 1 | Gas | 822
2023-05-17 11:00 | Western | 3 | HSD | 183
2023-05-17 11:00 | Western | 6 | Coal | 1712
2023-05-17 11:00 | Western | 8 | HVDC | 911
2023-05-17 11:00 | Western | 11 | Solar | 216.41
2023-05-17 12:00 | Eastern | 1 | Gas | 3903
2023-05-17 12:00 | Eastern | 2 | HFO | 1174
2023-05-17 12:00 | Eastern | 3 | HSD | 71
2023-05-17 12:00 | Eastern | 5 | Hydro | 25
2023-05-17 12:00 | Eastern | 10 | Tripura | 108
2023-05-17 12:00 | Eastern | 11 | Solar | 116
2023-05-17 12:00 | Western | 1 | Gas | 911
2023-05-17 12:00 | Western | 3 | HSD | 181
2023-05-17 12:00 | Western | 6 | Coal | 1663
2023-05-17 12:00 | Western | 8 | HVDC | 911
2023-05-17 12:00 | Western | 11 | Solar | 313.08
2023-05-17 13:00 | Eastern | 1 | Gas | 3941
2023-05-17 13:00 | Eastern | 2 | HFO | 1322
2023-05-17 13:00 | Eastern | 3 | HSD | 71
2023-05-17 13:00 | Eastern | 5 | Hydro | 25
2023-05-17 13:00 | Eastern | 10 | Tripura | 112
2023-05-17 13:00 | Eastern | 11 | Solar | 107
2023-05-17 13:00 | Western | 1 | Gas | 955
2023-05-17 13:00 | Western | 2 | HFO | 127
2023-05-17 13:00 | Western | 3 | HSD | 0
2023-05-17 13:00 | Western | 6 | Coal | 1790
2023-05-17 13:00 | Western | 8 | HVDC | 911
2023-05-17 13:00 | Western | 11 | Solar | 219.58
2023-05-17 14:00 | Eastern | 1 | Gas | 4037
2023-05-17 14:00 | Eastern | 2 | HFO | 1273
2023-05-17 14:00 | Eastern | 3 | HSD | 71
2023-05-17 14:00 | Eastern | 5 | Hydro | 25
2023-05-17 14:00 | Eastern | 10 | Tripura | 114
2023-05-17 14:00 | Eastern | 11 | Solar | 92
2023-05-17 14:00 | Western | 1 | Gas | 938
2023-05-17 14:00 | Western | 2 | HFO | 244
2023-05-17 14:00 | Western | 6 | Coal | 2050
2023-05-17 14:00 | Western | 8 | HVDC | 909
2023-05-17 14:00 | Western | 11 | Solar | 192.15
2023-05-17 15:00 | Eastern | 1 | Gas | 4034
2023-05-17 15:00 | Eastern | 2 | HFO | 1255
2023-05-17 15:00 | Eastern | 3 | HSD | 422
2023-05-17 15:00 | Eastern | 5 | Hydro | 25
2023-05-17 15:00 | Eastern | 10 | Tripura | 124
2023-05-17 15:00 | Eastern | 11 | Solar | 51
2023-05-17 15:00 | Western | 1 | Gas | 917
2023-05-17 15:00 | Western | 2 | HFO | 352
2023-05-17 15:00 | Western | 6 | Coal | 2100
2023-05-17 15:00 | Western | 8 | HVDC | 909
2023-05-17 15:00 | Western | 11 | Solar | 201.74
2023-05-17 16:00 | Eastern | 1 | Gas | 4072
2023-05-17 16:00 | Eastern | 2 | HFO | 1338
2023-05-17 16:00 | Eastern | 3 | HSD | 530
2023-05-17 16:00 | Eastern | 5 | Hydro | 25
2023-05-17 16:00 | Eastern | 10 | Tripura | 128
2023-05-17 16:00 | Eastern | 11 | Solar | 35
2023-05-17 16:00 | Western | 1 | Gas | 879
2023-05-17 16:00 | Western | 2 | HFO | 455
2023-05-17 16:00 | Western | 6 | Coal | 2155
2023-05-17 16:00 | Western | 8 | HVDC | 910
2023-05-17 16:00 | Western | 11 | Solar | 93.38
2023-05-17 17:00 | Eastern | 1 | Gas | 4052
2023-05-17 17:00 | Eastern | 2 | HFO | 1491.7
2023-05-17 17:00 | Eastern | 3 | HSD | 382
2023-05-17 17:00 | Eastern | 5 | Hydro | 25
2023-05-17 17:00 | Eastern | 10 | Tripura | 124
2023-05-17 17:00 | Eastern | 11 | Solar | 15
2023-05-17 17:00 | Western | 1 | Gas | 870
2023-05-17 17:00 | Western | 2 | HFO | 557
2023-05-17 17:00 | Western | 6 | Coal | 2109
2023-05-17 17:00 | Western | 8 | HVDC | 910
2023-05-17 17:00 | Western | 11 | Solar | 49.58
2023-05-17 18:00 | Eastern | 1 | Gas | 3945
2023-05-17 18:00 | Eastern | 2 | HFO | 1731
2023-05-17 18:00 | Eastern | 3 | HSD | 115
2023-05-17 18:00 | Eastern | 5 | Hydro | 25
2023-05-17 18:00 | Eastern | 10 | Tripura | 122
2023-05-17 18:00 | Eastern | 11 | Solar | 1
2023-05-17 18:00 | Western | 1 | Gas | 805
2023-05-17 18:00 | Western | 2 | HFO | 534
2023-05-17 18:00 | Western | 6 | Coal | 2027
2023-05-17 18:00 | Western | 8 | HVDC | 910
2023-05-17 18:00 | Western | 11 | Solar | 12.06
2023-05-17 19:00 | Eastern | 1 | Gas | 4195
2023-05-17 19:00 | Eastern | 2 | HFO | 2614
2023-05-17 19:00 | Eastern | 3 | HSD | 170
2023-05-17 19:00 | Eastern | 5 | Hydro | 25
2023-05-17 19:00 | Eastern | 10 | Tripura | 142
2023-05-17 19:00 | Eastern | 11 | Solar | 0
2023-05-17 19:00 | Western | 1 | Gas | 870
2023-05-17 19:00 | Western | 2 | HFO | 616
2023-05-17 19:00 | Western | 6 | Coal | 2111
2023-05-17 19:00 | Western | 8 | HVDC | 910
2023-05-17 19:00 | Western | 11 | Solar | 0
2023-05-17 19:30 | Eastern | 1 | Gas | 4227
2023-05-17 19:30 | Eastern | 2 | HFO | 2732
2023-05-17 19:30 | Eastern | 3 | HSD | 151
2023-05-17 19:30 | Eastern | 5 | Hydro | 25
2023-05-17 19:30 | Eastern | 10 | Tripura | 144
2023-05-17 19:30 | Western | 1 | Gas | 848
2023-05-17 19:30 | Western | 2 | HFO | 638
2023-05-17 19:30 | Western | 6 | Coal | 2275
2023-05-17 19:30 | Western | 8 | HVDC | 910
2023-05-17 20:00 | Eastern | 1 | Gas | 4120
2023-05-17 20:00 | Eastern | 2 | HFO | 2807
2023-05-17 20:00 | Eastern | 3 | HSD | 150
2023-05-17 20:00 | Eastern | 5 | Hydro | 25
2023-05-17 20:00 | Eastern | 10 | Tripura | 146
2023-05-17 20:00 | Western | 1 | Gas | 805
2023-05-17 20:00 | Western | 2 | HFO | 558
2023-05-17 20:00 | Western | 6 | Coal | 2157
2023-05-17 20:00 | Western | 8 | HVDC | 801
2023-05-17 21:00 | Eastern | 1 | Gas | 4215
2023-05-17 21:00 | Eastern | 2 | HFO | 2826
2023-05-17 21:00 | Eastern | 3 | HSD | 130
2023-05-17 21:00 | Eastern | 5 | Hydro | 25
2023-05-17 21:00 | Eastern | 10 | Tripura | 136
2023-05-17 21:00 | Western | 1 | Gas | 779
2023-05-17 21:00 | Western | 2 | HFO | 403
2023-05-17 21:00 | Western | 6 | Coal | 2060
2023-05-17 21:00 | Western | 8 | HVDC | 802
2023-05-17 22:00 | Eastern | 1 | Gas | 4230
2023-05-17 22:00 | Eastern | 2 | HFO | 2465
2023-05-17 22:00 | Eastern | 3 | HSD | 150
2023-05-17 22:00 | Eastern | 5 | Hydro | 25
2023-05-17 22:00 | Eastern | 10 | Tripura | 140
2023-05-17 22:00 | Western | 1 | Gas | 888
2023-05-17 22:00 | Western | 2 | HFO | 394
2023-05-17 22:00 | Western | 6 | Coal | 2063
2023-05-17 22:00 | Western | 8 | HVDC | 802
2023-05-17 23:00 | Eastern | 1 | Gas | 4532
2023-05-17 23:00 | Eastern | 2 | HFO | 1936
2023-05-17 23:00 | Eastern | 3 | HSD | 150
2023-05-17 23:00 | Eastern | 5 | Hydro | 0
2023-05-17 23:00 | Eastern | 10 | Tripura | 138
2023-05-17 23:00 | Western | 1 | Gas | 891
2023-05-17 23:00 | Western | 2 | HFO | 326
2023-05-17 23:00 | Western | 6 | Coal | 2176
2023-05-17 23:00 | Western | 8 | HVDC | 802
2023-05-18 | Eastern | 1 | Gas | 4492.5
2023-05-18 | Eastern | 2 | HFO | 1488
2023-05-18 | Eastern | 3 | HSD | 151
2023-05-18 | Eastern | 10 | Tripura | 134
2023-05-18 | Eastern | 11 | Solar | 0
2023-05-18 | Western | 1 | Gas | 880
2023-05-18 | Western | 2 | HFO | 406
2023-05-18 | Western | 6 | Coal | 2297
2023-05-18 | Western | 8 | HVDC | 804
2023-05-18 | Western | 11 | Solar | 0
2023-05-18 01:00 | Eastern | 1 | Gas | 4402.5
2023-05-18 01:00 | Eastern | 2 | HFO | 1178
2023-05-18 01:00 | Eastern | 3 | HSD | 152
2023-05-18 01:00 | Eastern | 10 | Tripura | 124
2023-05-18 01:00 | Western | 1 | Gas | 883
2023-05-18 01:00 | Western | 2 | HFO | 336
2023-05-18 01:00 | Western | 6 | Coal | 2268
2023-05-18 01:00 | Western | 8 | HVDC | 860
2023-05-18 02:00 | Eastern | 1 | Gas | 4306.5
2023-05-18 02:00 | Eastern | 2 | HFO | 1113
2023-05-18 02:00 | Eastern | 3 | HSD | 152
2023-05-18 02:00 | Eastern | 10 | Tripura | 126
2023-05-18 02:00 | Western | 1 | Gas | 832
2023-05-18 02:00 | Western | 2 | HFO | 333
2023-05-18 02:00 | Western | 6 | Coal | 1839
2023-05-18 02:00 | Western | 8 | HVDC | 860
2023-05-18 03:00 | Eastern | 1 | Gas | 4109
2023-05-18 03:00 | Eastern | 2 | HFO | 824
2023-05-18 03:00 | Eastern | 3 | HSD | 151
2023-05-18 03:00 | Eastern | 10 | Tripura | 124
2023-05-18 03:00 | Western | 1 | Gas | 840
2023-05-18 03:00 | Western | 2 | HFO | 0
2023-05-18 03:00 | Western | 6 | Coal | 1723
2023-05-18 03:00 | Western | 8 | HVDC | 860
2023-05-18 04:00 | Eastern | 1 | Gas | 3867
2023-05-18 04:00 | Eastern | 2 | HFO | 757
2023-05-18 04:00 | Eastern | 3 | HSD | 150
2023-05-18 04:00 | Eastern | 10 | Tripura | 112
2023-05-18 04:00 | Western | 1 | Gas | 712
2023-05-18 04:00 | Western | 6 | Coal | 1365
2023-05-18 04:00 | Western | 8 | HVDC | 895
2023-05-18 05:00 | Eastern | 1 | Gas | 3696
2023-05-18 05:00 | Eastern | 2 | HFO | 382
2023-05-18 05:00 | Eastern | 3 | HSD | 120
2023-05-18 05:00 | Eastern | 10 | Tripura | 110
2023-05-18 05:00 | Western | 1 | Gas | 681
2023-05-18 05:00 | Western | 6 | Coal | 1244
2023-05-18 05:00 | Western | 8 | HVDC | 821
2023-05-18 06:00 | Eastern | 1 | Gas | 2660
2023-05-18 06:00 | Eastern | 2 | HFO | 160
2023-05-18 06:00 | Eastern | 10 | Tripura | 102
2023-05-18 06:00 | Eastern | 11 | Solar | 0
2023-05-18 06:00 | Western | 1 | Gas | 686
2023-05-18 06:00 | Western | 6 | Coal | 1199
2023-05-18 06:00 | Western | 8 | HVDC | 151
2023-05-18 06:00 | Western | 11 | Solar | 1
2023-05-18 07:00 | Eastern | 1 | Gas | 2602
2023-05-18 07:00 | Eastern | 2 | HFO | 271
2023-05-18 07:00 | Eastern | 10 | Tripura | 30
2023-05-18 07:00 | Eastern | 11 | Solar | 7
2023-05-18 07:00 | Western | 1 | Gas | 615
2023-05-18 07:00 | Western | 2 | HFO | 0
2023-05-18 07:00 | Western | 6 | Coal | 1195
2023-05-18 07:00 | Western | 8 | HVDC | 601
2023-05-18 07:00 | Western | 11 | Solar | 19
2023-05-18 08:00 | Eastern | 1 | Gas | 3073
2023-05-18 08:00 | Eastern | 2 | HFO | 303
2023-05-18 08:00 | Eastern | 10 | Tripura | 72
2023-05-18 08:00 | Eastern | 11 | Solar | 22
2023-05-18 08:00 | Western | 1 | Gas | 674
2023-05-18 08:00 | Western | 6 | Coal | 1220
2023-05-18 08:00 | Western | 8 | HVDC | 907
2023-05-18 08:00 | Western | 11 | Solar | 24.53
2023-05-18 09:00 | Eastern | 1 | Gas | 3469
2023-05-18 09:00 | Eastern | 2 | HFO | 436
2023-05-18 09:00 | Eastern | 10 | Tripura | 82
2023-05-18 09:00 | Eastern | 11 | Solar | 59
2023-05-18 09:00 | Western | 1 | Gas | 708
2023-05-18 09:00 | Western | 6 | Coal | 1275
2023-05-18 09:00 | Western | 8 | HVDC | 908
2023-05-18 09:00 | Western | 11 | Solar | 78.1
2023-05-18 10:00 | Eastern | 1 | Gas | 3859
2023-05-18 10:00 | Eastern | 2 | HFO | 620
2023-05-18 10:00 | Eastern | 5 | Hydro | 0
2023-05-18 10:00 | Eastern | 10 | Tripura | 92
2023-05-18 10:00 | Eastern | 11 | Solar | 87
2023-05-18 10:00 | Western | 1 | Gas | 695
2023-05-18 10:00 | Western | 2 | HFO | 68
2023-05-18 10:00 | Western | 6 | Coal | 1371
2023-05-18 10:00 | Western | 8 | HVDC | 906
2023-05-18 10:00 | Western | 11 | Solar | 209.83
2023-05-18 11:00 | Eastern | 1 | Gas | 4048
2023-05-18 11:00 | Eastern | 2 | HFO | 1166
2023-05-18 11:00 | Eastern | 5 | Hydro | 25
2023-05-18 11:00 | Eastern | 10 | Tripura | 114
2023-05-18 11:00 | Eastern | 11 | Solar | 87
2023-05-18 11:00 | Western | 1 | Gas | 764
2023-05-18 11:00 | Western | 2 | HFO | 313
2023-05-18 11:00 | Western | 6 | Coal | 1455
2023-05-18 11:00 | Western | 8 | HVDC | 907
2023-05-18 11:00 | Western | 11 | Solar | 121.37
2023-05-18 12:00 | Eastern | 1 | Gas | 4121
2023-05-18 12:00 | Eastern | 2 | HFO | 1391
2023-05-18 12:00 | Eastern | 3 | HSD | 370
2023-05-18 12:00 | Eastern | 5 | Hydro | 25
2023-05-18 12:00 | Eastern | 10 | Tripura | 118
2023-05-18 12:00 | Eastern | 11 | Solar | 76
2023-05-18 12:00 | Western | 1 | Gas | 776
2023-05-18 12:00 | Western | 2 | HFO | 371
2023-05-18 12:00 | Western | 6 | Coal | 1576
2023-05-18 12:00 | Western | 8 | HVDC | 907
2023-05-18 12:00 | Western | 11 | Solar | 124.4
2023-05-18 13:00 | Eastern | 1 | Gas | 4010
2023-05-18 13:00 | Eastern | 2 | HFO | 1446
2023-05-18 13:00 | Eastern | 3 | HSD | 413
2023-05-18 13:00 | Eastern | 5 | Hydro | 25
2023-05-18 13:00 | Eastern | 10 | Tripura | 128
2023-05-18 13:00 | Eastern | 11 | Solar | 69
2023-05-18 13:00 | Western | 1 | Gas | 773
2023-05-18 13:00 | Western | 2 | HFO | 375
2023-05-18 13:00 | Western | 6 | Coal | 1738
2023-05-18 13:00 | Western | 8 | HVDC | 948
2023-05-18 13:00 | Western | 11 | Solar | 252.09
2023-05-18 14:00 | Eastern | 1 | Gas | 4127
2023-05-18 14:00 | Eastern | 2 | HFO | 1326
2023-05-18 14:00 | Eastern | 3 | HSD | 366
2023-05-18 14:00 | Eastern | 5 | Hydro | 25
2023-05-18 14:00 | Eastern | 10 | Tripura | 128
2023-05-18 14:00 | Eastern | 11 | Solar | 59
2023-05-18 14:00 | Western | 1 | Gas | 758
2023-05-18 14:00 | Western | 2 | HFO | 399
2023-05-18 14:00 | Western | 6 | Coal | 1826
2023-05-18 14:00 | Western | 8 | HVDC | 907
2023-05-18 14:00 | Western | 11 | Solar | 137.71
2023-05-18 15:00 | Eastern | 1 | Gas | 4066
2023-05-18 15:00 | Eastern | 2 | HFO | 1269
2023-05-18 15:00 | Eastern | 3 | HSD | 448
2023-05-18 15:00 | Eastern | 5 | Hydro | 25
2023-05-18 15:00 | Eastern | 10 | Tripura | 132
2023-05-18 15:00 | Eastern | 11 | Solar | 51
2023-05-18 15:00 | Western | 1 | Gas | 766
2023-05-18 15:00 | Western | 2 | HFO | 434
2023-05-18 15:00 | Western | 6 | Coal | 1865
2023-05-18 15:00 | Western | 8 | HVDC | 907
2023-05-18 15:00 | Western | 11 | Solar | 114.01
2023-05-18 16:00 | Eastern | 1 | Gas | 4011
2023-05-18 16:00 | Eastern | 2 | HFO | 1338
2023-05-18 16:00 | Eastern | 3 | HSD | 444
2023-05-18 16:00 | Eastern | 5 | Hydro | 25
2023-05-18 16:00 | Eastern | 10 | Tripura | 142
2023-05-18 16:00 | Eastern | 11 | Solar | 41
2023-05-18 16:00 | Western | 1 | Gas | 773
2023-05-18 16:00 | Western | 2 | HFO | 471
2023-05-18 16:00 | Western | 6 | Coal | 1930
2023-05-18 16:00 | Western | 8 | HVDC | 895
2023-05-18 16:00 | Western | 11 | Solar | 146.64
2023-05-18 17:00 | Eastern | 1 | Gas | 4067
2023-05-18 17:00 | Eastern | 2 | HFO | 1489
2023-05-18 17:00 | Eastern | 3 | HSD | 394
2023-05-18 17:00 | Eastern | 5 | Hydro | 25
2023-05-18 17:00 | Eastern | 10 | Tripura | 134
2023-05-18 17:00 | Eastern | 11 | Solar | 16
2023-05-18 17:00 | Western | 1 | Gas | 768
2023-05-18 17:00 | Western | 2 | HFO | 567
2023-05-18 17:00 | Western | 6 | Coal | 1949
2023-05-18 17:00 | Western | 8 | HVDC | 894
2023-05-18 17:00 | Western | 11 | Solar | 58.45
2023-05-18 18:00 | Eastern | 1 | Gas | 4037
2023-05-18 18:00 | Eastern | 2 | HFO | 1831
2023-05-18 18:00 | Eastern | 3 | HSD | 108
2023-05-18 18:00 | Eastern | 5 | Hydro | 25
2023-05-18 18:00 | Eastern | 10 | Tripura | 114
2023-05-18 18:00 | Eastern | 11 | Solar | 1
2023-05-18 18:00 | Western | 1 | Gas | 720
2023-05-18 18:00 | Western | 2 | HFO | 605
2023-05-18 18:00 | Western | 6 | Coal | 1983
2023-05-18 18:00 | Western | 8 | HVDC | 902
2023-05-18 18:00 | Western | 11 | Solar | 9
2023-05-18 19:00 | Eastern | 1 | Gas | 4132
2023-05-18 19:00 | Eastern | 2 | HFO | 2503
2023-05-18 19:00 | Eastern | 3 | HSD | 220
2023-05-18 19:00 | Eastern | 5 | Hydro | 25
2023-05-18 19:00 | Eastern | 10 | Tripura | 138
2023-05-18 19:00 | Eastern | 11 | Solar | 0
2023-05-18 19:00 | Western | 1 | Gas | 775
2023-05-18 19:00 | Western | 2 | HFO | 760.5
2023-05-18 19:00 | Western | 6 | Coal | 2190
2023-05-18 19:00 | Western | 8 | HVDC | 902
2023-05-18 19:00 | Western | 11 | Solar | 0
2023-05-18 19:30 | Eastern | 1 | Gas | 4092
2023-05-18 19:30 | Eastern | 2 | HFO | 2653
2023-05-18 19:30 | Eastern | 3 | HSD | 211
2023-05-18 19:30 | Eastern | 5 | Hydro | 25
2023-05-18 19:30 | Eastern | 10 | Tripura | 138
2023-05-18 19:30 | Western | 1 | Gas | 754
2023-05-18 19:30 | Western | 2 | HFO | 747
2023-05-18 19:30 | Western | 6 | Coal | 2302
2023-05-18 19:30 | Western | 8 | HVDC | 905
2023-05-18 20:00 | Eastern | 1 | Gas | 4173
2023-05-18 20:00 | Eastern | 2 | HFO | 2635
2023-05-18 20:00 | Eastern | 3 | HSD | 224
2023-05-18 20:00 | Eastern | 5 | Hydro | 25
2023-05-18 20:00 | Eastern | 10 | Tripura | 136
2023-05-18 20:00 | Western | 1 | Gas | 768
2023-05-18 20:00 | Western | 2 | HFO | 594
2023-05-18 20:00 | Western | 6 | Coal | 2329
2023-05-18 20:00 | Western | 8 | HVDC | 810
2023-05-18 21:00 | Eastern | 1 | Gas | 4201
2023-05-18 21:00 | Eastern | 2 | HFO | 2651
2023-05-18 21:00 | Eastern | 3 | HSD | 226
2023-05-18 21:00 | Eastern | 5 | Hydro | 25
2023-05-18 21:00 | Eastern | 10 | Tripura | 138
2023-05-18 21:00 | Western | 1 | Gas | 779
2023-05-18 21:00 | Western | 2 | HFO | 587
2023-05-18 21:00 | Western | 6 | Coal | 2372
2023-05-18 21:00 | Western | 8 | HVDC | 810
2023-05-18 22:00 | Eastern | 1 | Gas | 4261
2023-05-18 22:00 | Eastern | 2 | HFO | 2403
2023-05-18 22:00 | Eastern | 3 | HSD | 227
2023-05-18 22:00 | Eastern | 5 | Hydro | 25
2023-05-18 22:00 | Eastern | 10 | Tripura | 138
2023-05-18 22:00 | Western | 1 | Gas | 781
2023-05-18 22:00 | Western | 2 | HFO | 580
2023-05-18 22:00 | Western | 6 | Coal | 2418
2023-05-18 22:00 | Western | 8 | HVDC | 810
2023-05-18 23:00 | Eastern | 1 | Gas | 4334.5
2023-05-18 23:00 | Eastern | 2 | HFO | 1947
2023-05-18 23:00 | Eastern | 3 | HSD | 222
2023-05-18 23:00 | Eastern | 5 | Hydro | 0
2023-05-18 23:00 | Eastern | 10 | Tripura | 138
2023-05-18 23:00 | Western | 1 | Gas | 778
2023-05-18 23:00 | Western | 2 | HFO | 501
2023-05-18 23:00 | Western | 6 | Coal | 2459
2023-05-18 23:00 | Western | 8 | HVDC | 795
2023-05-19 | Eastern | 1 | Gas | 4197.5
2023-05-19 | Eastern | 2 | HFO | 1565
2023-05-19 | Eastern | 3 | HSD | 412
2023-05-19 | Eastern | 10 | Tripura | 126
2023-05-19 | Eastern | 11 | Solar | 0
2023-05-19 | Western | 1 | Gas | 789
2023-05-19 | Western | 2 | HFO | 514
2023-05-19 | Western | 6 | Coal | 2482
2023-05-19 | Western | 8 | HVDC | 795
2023-05-19 01:00 | Eastern | 1 | Gas | 4238
2023-05-19 01:00 | Eastern | 2 | HFO | 1265
2023-05-19 01:00 | Eastern | 3 | HSD | 422
2023-05-19 01:00 | Eastern | 10 | Tripura | 126
2023-05-19 01:00 | Western | 1 | Gas | 789
2023-05-19 01:00 | Western | 2 | HFO | 442
2023-05-19 01:00 | Western | 6 | Coal | 2397
2023-05-19 01:00 | Western | 8 | HVDC | 815
2023-05-19 02:00 | Eastern | 1 | Gas | 4245
2023-05-19 02:00 | Eastern | 2 | HFO | 1185
2023-05-19 02:00 | Eastern | 3 | HSD | 226
2023-05-19 02:00 | Eastern | 10 | Tripura | 120
2023-05-19 02:00 | Western | 1 | Gas | 781
2023-05-19 02:00 | Western | 2 | HFO | 442
2023-05-19 02:00 | Western | 6 | Coal | 2322
2023-05-19 02:00 | Western | 8 | HVDC | 815
2023-05-19 03:00 | Eastern | 1 | Gas | 4259
2023-05-19 03:00 | Eastern | 2 | HFO | 1001
2023-05-19 03:00 | Eastern | 3 | HSD | 227
2023-05-19 03:00 | Eastern | 10 | Tripura | 116
2023-05-19 03:00 | Western | 1 | Gas | 782
2023-05-19 03:00 | Western | 2 | HFO | 241
2023-05-19 03:00 | Western | 6 | Coal | 2262
2023-05-19 03:00 | Western | 8 | HVDC | 911
2023-05-19 04:00 | Eastern | 1 | Gas | 4231
2023-05-19 04:00 | Eastern | 2 | HFO | 800
2023-05-19 04:00 | Eastern | 3 | HSD | 227
2023-05-19 04:00 | Eastern | 10 | Tripura | 118
2023-05-19 04:00 | Western | 1 | Gas | 788
2023-05-19 04:00 | Western | 2 | HFO | 109
2023-05-19 04:00 | Western | 6 | Coal | 2240
2023-05-19 04:00 | Western | 8 | HVDC | 910
2023-05-19 05:00 | Eastern | 1 | Gas | 4114
2023-05-19 05:00 | Eastern | 2 | HFO | 798
2023-05-19 05:00 | Eastern | 3 | HSD | 227
2023-05-19 05:00 | Eastern | 10 | Tripura | 112
2023-05-19 05:00 | Eastern | 11 | Solar | 0
2023-05-19 05:00 | Western | 1 | Gas | 749
2023-05-19 05:00 | Western | 2 | HFO | 52
2023-05-19 05:00 | Western | 6 | Coal | 2138
2023-05-19 05:00 | Western | 8 | HVDC | 909
2023-05-19 05:00 | Western | 11 | Solar | 0
2023-05-19 06:00 | Eastern | 1 | Gas | 4001
2023-05-19 06:00 | Eastern | 2 | HFO | 748
2023-05-19 06:00 | Eastern | 3 | HSD | 227
2023-05-19 06:00 | Eastern | 10 | Tripura | 84
2023-05-19 06:00 | Eastern | 11 | Solar | 5
2023-05-19 06:00 | Western | 1 | Gas | 749
2023-05-19 06:00 | Western | 2 | HFO | 58
2023-05-19 06:00 | Western | 6 | Coal | 1922
2023-05-19 06:00 | Western | 8 | HVDC | 907
2023-05-19 06:00 | Western | 11 | Solar | 6.14
2023-05-19 07:00 | Eastern | 1 | Gas | 4060
2023-05-19 07:00 | Eastern | 2 | HFO | 752
2023-05-19 07:00 | Eastern | 3 | HSD | 223
2023-05-19 07:00 | Eastern | 10 | Tripura | 92
2023-05-19 07:00 | Eastern | 11 | Solar | 9
2023-05-19 07:00 | Western | 1 | Gas | 755
2023-05-19 07:00 | Western | 2 | HFO | 17
2023-05-19 07:00 | Western | 6 | Coal | 1857
2023-05-19 07:00 | Western | 8 | HVDC | 907
2023-05-19 07:00 | Western | 11 | Solar | 28.89
2023-05-19 08:00 | Eastern | 1 | Gas | 4036
2023-05-19 08:00 | Eastern | 2 | HFO | 758
2023-05-19 08:00 | Eastern | 3 | HSD | 221
2023-05-19 08:00 | Eastern | 10 | Tripura | 90
2023-05-19 08:00 | Eastern | 11 | Solar | 31
2023-05-19 08:00 | Western | 1 | Gas | 760
2023-05-19 08:00 | Western | 2 | HFO | 43
2023-05-19 08:00 | Western | 6 | Coal | 1820
2023-05-19 08:00 | Western | 8 | HVDC | 911
2023-05-19 08:00 | Western | 11 | Solar | 79.86
2023-05-19 09:00 | Eastern | 1 | Gas | 4145
2023-05-19 09:00 | Eastern | 2 | HFO | 774
2023-05-19 09:00 | Eastern | 3 | HSD | 218
2023-05-19 09:00 | Eastern | 10 | Tripura | 106
2023-05-19 09:00 | Eastern | 11 | Solar | 84
2023-05-19 09:00 | Western | 1 | Gas | 772
2023-05-19 09:00 | Western | 2 | HFO | 98
2023-05-19 09:00 | Western | 6 | Coal | 1816
2023-05-19 09:00 | Western | 8 | HVDC | 911
2023-05-19 09:00 | Western | 11 | Solar | 112.02
2023-05-19 10:00 | Eastern | 1 | Gas | 4154
2023-05-19 10:00 | Eastern | 2 | HFO | 854
2023-05-19 10:00 | Eastern | 3 | HSD | 216
2023-05-19 10:00 | Eastern | 5 | Hydro | 25
2023-05-19 10:00 | Eastern | 10 | Tripura | 110
2023-05-19 10:00 | Eastern | 11 | Solar | 66
2023-05-19 10:00 | Western | 1 | Gas | 798
2023-05-19 10:00 | Western | 2 | HFO | 162
2023-05-19 10:00 | Western | 6 | Coal | 1810
2023-05-19 10:00 | Western | 8 | HVDC | 911
2023-05-19 10:00 | Western | 11 | Solar | 127.19
2023-05-19 11:00 | Eastern | 1 | Gas | 4067.5
2023-05-19 11:00 | Eastern | 2 | HFO | 1089
2023-05-19 11:00 | Eastern | 3 | HSD | 424
2023-05-19 11:00 | Eastern | 5 | Hydro | 25
2023-05-19 11:00 | Eastern | 10 | Tripura | 110
2023-05-19 11:00 | Eastern | 11 | Solar | 58
2023-05-19 11:00 | Western | 1 | Gas | 867
2023-05-19 11:00 | Western | 2 | HFO | 230
2023-05-19 11:00 | Western | 6 | Coal | 1864
2023-05-19 11:00 | Western | 8 | HVDC | 911
2023-05-19 11:00 | Western | 11 | Solar | 155.76
2023-05-19 12:00 | Eastern | 1 | Gas | 4170.5
2023-05-19 12:00 | Eastern | 2 | HFO | 1212
2023-05-19 12:00 | Eastern | 3 | HSD | 428
2023-05-19 12:00 | Eastern | 5 | Hydro | 25
2023-05-19 12:00 | Eastern | 10 | Tripura | 118
2023-05-19 12:00 | Eastern | 11 | Solar | 54
2023-05-19 12:00 | Western | 1 | Gas | 919
2023-05-19 12:00 | Western | 2 | HFO | 381
2023-05-19 12:00 | Western | 6 | Coal | 1893
2023-05-19 12:00 | Western | 8 | HVDC | 911
2023-05-19 12:00 | Western | 11 | Solar | 167.16
2023-05-19 13:00 | Eastern | 1 | Gas | 4057
2023-05-19 13:00 | Eastern | 2 | HFO | 1246
2023-05-19 13:00 | Eastern | 3 | HSD | 590
2023-05-19 13:00 | Eastern | 5 | Hydro | 25
2023-05-19 13:00 | Eastern | 10 | Tripura | 126
2023-05-19 13:00 | Eastern | 11 | Solar | 53
2023-05-19 13:00 | Western | 1 | Gas | 951
2023-05-19 13:00 | Western | 2 | HFO | 462
2023-05-19 13:00 | Western | 6 | Coal | 1926
2023-05-19 13:00 | Western | 8 | HVDC | 910
2023-05-19 13:00 | Western | 11 | Solar | 148.95
2023-05-19 14:00 | Eastern | 1 | Gas | 4156
2023-05-19 14:00 | Eastern | 2 | HFO | 1173
2023-05-19 14:00 | Eastern | 3 | HSD | 323
2023-05-19 14:00 | Eastern | 5 | Hydro | 25
2023-05-19 14:00 | Eastern | 10 | Tripura | 144
2023-05-19 14:00 | Eastern | 11 | Solar | 64
2023-05-19 14:00 | Western | 1 | Gas | 970
2023-05-19 14:00 | Western | 2 | HFO | 417
2023-05-19 14:00 | Western | 6 | Coal | 1896
2023-05-19 14:00 | Western | 8 | HVDC | 912
2023-05-19 14:00 | Western | 11 | Solar | 176
2023-05-19 15:00 | Eastern | 1 | Gas | 4220
2023-05-19 15:00 | Eastern | 2 | HFO | 1135
2023-05-19 15:00 | Eastern | 3 | HSD | 580
2023-05-19 15:00 | Eastern | 5 | Hydro | 25
2023-05-19 15:00 | Eastern | 10 | Tripura | 150
2023-05-19 15:00 | Eastern | 11 | Solar | 55
2023-05-19 15:00 | Western | 1 | Gas | 963
2023-05-19 15:00 | Western | 2 | HFO | 421
2023-05-19 15:00 | Western | 6 | Coal | 1927
2023-05-19 15:00 | Western | 8 | HVDC | 910
2023-05-19 15:00 | Western | 11 | Solar | 127.72
2023-05-19 16:00 | Eastern | 1 | Gas | 4277
2023-05-19 16:00 | Eastern | 2 | HFO | 1259
2023-05-19 16:00 | Eastern | 3 | HSD | 410
2023-05-19 16:00 | Eastern | 5 | Hydro | 25
2023-05-19 16:00 | Eastern | 10 | Tripura | 136
2023-05-19 16:00 | Eastern | 11 | Solar | 38
2023-05-19 16:00 | Western | 1 | Gas | 956
2023-05-19 16:00 | Western | 2 | HFO | 422
2023-05-19 16:00 | Western | 6 | Coal | 2013
2023-05-19 16:00 | Western | 8 | HVDC | 910
2023-05-19 16:00 | Western | 11 | Solar | 126.75
2023-05-19 17:00 | Eastern | 1 | Gas | 4199
2023-05-19 17:00 | Eastern | 2 | HFO | 1477
2023-05-19 17:00 | Eastern | 3 | HSD | 220
2023-05-19 17:00 | Eastern | 5 | Hydro | 25
2023-05-19 17:00 | Eastern | 10 | Tripura | 132
2023-05-19 17:00 | Eastern | 11 | Solar | 20
2023-05-19 17:00 | Western | 1 | Gas | 897
2023-05-19 17:00 | Western | 2 | HFO | 357
2023-05-19 17:00 | Western | 6 | Coal | 2014
2023-05-19 17:00 | Western | 8 | HVDC | 911
2023-05-19 17:00 | Western | 11 | Solar | 48.07
2023-05-19 18:00 | Eastern | 1 | Gas | 3838
2023-05-19 18:00 | Eastern | 2 | HFO | 1606
2023-05-19 18:00 | Eastern | 3 | HSD | 181
2023-05-19 18:00 | Eastern | 5 | Hydro | 25
2023-05-19 18:00 | Eastern | 10 | Tripura | 128
2023-05-19 18:00 | Eastern | 11 | Solar | 2
2023-05-19 18:00 | Western | 1 | Gas | 773
2023-05-19 18:00 | Western | 2 | HFO | 349
2023-05-19 18:00 | Western | 6 | Coal | 2015
2023-05-19 18:00 | Western | 8 | HVDC | 912
2023-05-19 18:00 | Western | 11 | Solar | 11.07
2023-05-19 19:00 | Eastern | 1 | Gas | 4277.5
2023-05-19 19:00 | Eastern | 2 | HFO | 2334
2023-05-19 19:00 | Eastern | 3 | HSD | 405
2023-05-19 19:00 | Eastern | 5 | Hydro | 25
2023-05-19 19:00 | Eastern | 10 | Tripura | 160
2023-05-19 19:00 | Western | 1 | Gas | 888
2023-05-19 19:00 | Western | 2 | HFO | 695
2023-05-19 19:00 | Western | 6 | Coal | 2210
2023-05-19 19:00 | Western | 8 | HVDC | 911
2023-05-19 19:00 | Western | 11 | Solar | 0
2023-05-19 19:30 | Eastern | 1 | Gas | 4275.5
2023-05-19 19:30 | Eastern | 2 | HFO | 2722
2023-05-19 19:30 | Eastern | 3 | HSD | 221
2023-05-19 19:30 | Eastern | 5 | Hydro | 25
2023-05-19 19:30 | Eastern | 10 | Tripura | 144
2023-05-19 19:30 | Western | 1 | Gas | 956
2023-05-19 19:30 | Western | 2 | HFO | 910
2023-05-19 19:30 | Western | 6 | Coal | 2450
2023-05-19 19:30 | Western | 8 | HVDC | 911
2023-05-19 20:00 | Eastern | 1 | Gas | 4299.5
2023-05-19 20:00 | Eastern | 2 | HFO | 2723
2023-05-19 20:00 | Eastern | 3 | HSD | 221
2023-05-19 20:00 | Eastern | 5 | Hydro | 25
2023-05-19 20:00 | Eastern | 10 | Tripura | 144
2023-05-19 20:00 | Western | 1 | Gas | 905
2023-05-19 20:00 | Western | 2 | HFO | 935
2023-05-19 20:00 | Western | 6 | Coal | 2479
2023-05-19 20:00 | Western | 8 | HVDC | 910
2023-05-19 21:00 | Eastern | 1 | Gas | 4431.5
2023-05-19 21:00 | Eastern | 2 | HFO | 2650
2023-05-19 21:00 | Eastern | 3 | HSD | 222
2023-05-19 21:00 | Eastern | 5 | Hydro | 25
2023-05-19 21:00 | Eastern | 10 | Tripura | 136
2023-05-19 21:00 | Western | 1 | Gas | 911
2023-05-19 21:00 | Western | 2 | HFO | 744
2023-05-19 21:00 | Western | 6 | Coal | 2608
2023-05-19 21:00 | Western | 8 | HVDC | 910
2023-05-19 22:00 | Eastern | 1 | Gas | 4462
2023-05-19 22:00 | Eastern | 2 | HFO | 2560
2023-05-19 22:00 | Eastern | 3 | HSD | 220
2023-05-19 22:00 | Eastern | 5 | Hydro | 25
2023-05-19 22:00 | Eastern | 10 | Tripura | 144
2023-05-19 22:00 | Western | 1 | Gas | 841
2023-05-19 22:00 | Western | 2 | HFO | 612
2023-05-19 22:00 | Western | 6 | Coal | 2512
2023-05-19 22:00 | Western | 8 | HVDC | 909
2023-05-19 23:00 | Eastern | 1 | Gas | 4672
2023-05-19 23:00 | Eastern | 2 | HFO | 2048
2023-05-19 23:00 | Eastern | 3 | HSD | 219
2023-05-19 23:00 | Eastern | 5 | Hydro | 0
2023-05-19 23:00 | Eastern | 10 | Tripura | 158
2023-05-19 23:00 | Western | 1 | Gas | 871
2023-05-19 23:00 | Western | 2 | HFO | 537
2023-05-19 23:00 | Western | 6 | Coal | 2444
2023-05-19 23:00 | Western | 8 | HVDC | 767
2023-05-20 | Eastern | 1 | Gas | 4721
2023-05-20 | Eastern | 2 | HFO | 1569
2023-05-20 | Eastern | 3 | HSD | 638
2023-05-20 | Eastern | 10 | Tripura | 144
2023-05-20 | Eastern | 11 | Solar | 0
2023-05-20 | Western | 1 | Gas | 933
2023-05-20 | Western | 2 | HFO | 547
2023-05-20 | Western | 6 | Coal | 2464
2023-05-20 | Western | 8 | HVDC | 768
2023-05-20 01:00 | Eastern | 1 | Gas | 4705
2023-05-20 01:00 | Eastern | 2 | HFO | 1110
2023-05-20 01:00 | Eastern | 3 | HSD | 495
2023-05-20 01:00 | Eastern | 10 | Tripura | 140
2023-05-20 01:00 | Western | 1 | Gas | 945
2023-05-20 01:00 | Western | 2 | HFO | 439
2023-05-20 01:00 | Western | 6 | Coal | 2429
2023-05-20 01:00 | Western | 8 | HVDC | 805
2023-05-20 02:00 | Eastern | 1 | Gas | 4612
2023-05-20 02:00 | Eastern | 2 | HFO | 891
2023-05-20 02:00 | Eastern | 3 | HSD | 220
2023-05-20 02:00 | Eastern | 10 | Tripura | 150
2023-05-20 02:00 | Western | 1 | Gas | 903
2023-05-20 02:00 | Western | 2 | HFO | 192
2023-05-20 02:00 | Western | 6 | Coal | 2380
2023-05-20 02:00 | Western | 8 | HVDC | 805
2023-05-20 03:00 | Eastern | 1 | Gas | 4480
2023-05-20 03:00 | Eastern | 2 | HFO | 694
2023-05-20 03:00 | Eastern | 3 | HSD | 222
2023-05-20 03:00 | Eastern | 10 | Tripura | 150
2023-05-20 03:00 | Western | 1 | Gas | 855
2023-05-20 03:00 | Western | 2 | HFO | 17
2023-05-20 03:00 | Western | 6 | Coal | 2190
2023-05-20 03:00 | Western | 8 | HVDC | 910
2023-05-20 04:00 | Eastern | 1 | Gas | 4134
2023-05-20 04:00 | Eastern | 2 | HFO | 671
2023-05-20 04:00 | Eastern | 3 | HSD | 219
2023-05-20 04:00 | Eastern | 10 | Tripura | 150
2023-05-20 04:00 | Western | 1 | Gas | 846
2023-05-20 04:00 | Western | 2 | HFO | 17
2023-05-20 04:00 | Western | 6 | Coal | 2169
2023-05-20 04:00 | Western | 8 | HVDC | 910
2023-05-20 05:00 | Eastern | 1 | Gas | 4096
2023-05-20 05:00 | Eastern | 2 | HFO | 627
2023-05-20 05:00 | Eastern | 3 | HSD | 225
2023-05-20 05:00 | Eastern | 10 | Tripura | 150
2023-05-20 05:00 | Eastern | 11 | Solar | 0
2023-05-20 05:00 | Western | 1 | Gas | 844
2023-05-20 05:00 | Western | 2 | HFO | 17
2023-05-20 05:00 | Western | 6 | Coal | 2089
2023-05-20 05:00 | Western | 8 | HVDC | 910
2023-05-20 05:00 | Western | 11 | Solar | 0
2023-05-20 06:00 | Eastern | 1 | Gas | 3970
2023-05-20 06:00 | Eastern | 2 | HFO | 525
2023-05-20 06:00 | Eastern | 3 | HSD | 222
2023-05-20 06:00 | Eastern | 10 | Tripura | 132
2023-05-20 06:00 | Eastern | 11 | Solar | 6
2023-05-20 06:00 | Western | 1 | Gas | 820
2023-05-20 06:00 | Western | 2 | HFO | 0
2023-05-20 06:00 | Western | 6 | Coal | 2010
2023-05-20 06:00 | Western | 8 | HVDC | 911
2023-05-20 06:00 | Western | 11 | Solar | 13
2023-05-20 07:00 | Eastern | 1 | Gas | 4003
2023-05-20 07:00 | Eastern | 2 | HFO | 541
2023-05-20 07:00 | Eastern | 3 | HSD | 221
2023-05-20 07:00 | Eastern | 10 | Tripura | 134
2023-05-20 07:00 | Eastern | 11 | Solar | 28
2023-05-20 07:00 | Western | 1 | Gas | 749
2023-05-20 07:00 | Western | 6 | Coal | 2014
2023-05-20 07:00 | Western | 8 | HVDC | 910
2023-05-20 07:00 | Western | 11 | Solar | 76.15
2023-05-20 08:00 | Eastern | 1 | Gas | 4093
2023-05-20 08:00 | Eastern | 2 | HFO | 546
2023-05-20 08:00 | Eastern | 3 | HSD | 218
2023-05-20 08:00 | Eastern | 10 | Tripura | 136
2023-05-20 08:00 | Eastern | 11 | Solar | 59
2023-05-20 08:00 | Western | 1 | Gas | 760
2023-05-20 08:00 | Western | 6 | Coal | 2013
2023-05-20 08:00 | Western | 8 | HVDC | 912
2023-05-20 08:00 | Western | 11 | Solar | 165.44
2023-05-20 09:00 | Eastern | 1 | Gas | 4303
2023-05-20 09:00 | Eastern | 2 | HFO | 575
2023-05-20 09:00 | Eastern | 3 | HSD | 220
2023-05-20 09:00 | Eastern | 5 | Hydro | 0
2023-05-20 09:00 | Eastern | 10 | Tripura | 120
2023-05-20 09:00 | Eastern | 11 | Solar | 68
2023-05-20 09:00 | Western | 1 | Gas | 871
2023-05-20 09:00 | Western | 2 | HFO | 0
2023-05-20 09:00 | Western | 6 | Coal | 2056
2023-05-20 09:00 | Western | 8 | HVDC | 911
2023-05-20 09:00 | Western | 11 | Solar | 208.12
2023-05-20 10:00 | Eastern | 1 | Gas | 4474
2023-05-20 10:00 | Eastern | 2 | HFO | 738
2023-05-20 10:00 | Eastern | 3 | HSD | 215
2023-05-20 10:00 | Eastern | 5 | Hydro | 25
2023-05-20 10:00 | Eastern | 10 | Tripura | 130
2023-05-20 10:00 | Eastern | 11 | Solar | 91
2023-05-20 10:00 | Western | 1 | Gas | 890
2023-05-20 10:00 | Western | 2 | HFO | 65
2023-05-20 10:00 | Western | 6 | Coal | 2067
2023-05-20 10:00 | Western | 8 | HVDC | 912
2023-05-20 10:00 | Western | 11 | Solar | 284.04
2023-05-20 11:00 | Eastern | 1 | Gas | 4491
2023-05-20 11:00 | Eastern | 2 | HFO | 1084
2023-05-20 11:00 | Eastern | 3 | HSD | 367
2023-05-20 11:00 | Eastern | 5 | Hydro | 25
2023-05-20 11:00 | Eastern | 10 | Tripura | 156
2023-05-20 11:00 | Eastern | 11 | Solar | 95
2023-05-20 11:00 | Western | 1 | Gas | 858
2023-05-20 11:00 | Western | 2 | HFO | 160
2023-05-20 11:00 | Western | 6 | Coal | 2116
2023-05-20 11:00 | Western | 8 | HVDC | 911
2023-05-20 11:00 | Western | 11 | Solar | 334.93
2023-05-20 12:00 | Eastern | 1 | Gas | 4629
2023-05-20 12:00 | Eastern | 2 | HFO | 1090
2023-05-20 12:00 | Eastern | 3 | HSD | 286
2023-05-20 12:00 | Eastern | 5 | Hydro | 25
2023-05-20 12:00 | Eastern | 10 | Tripura | 148
2023-05-20 12:00 | Eastern | 11 | Solar | 103
2023-05-20 12:00 | Western | 1 | Gas | 856
2023-05-20 12:00 | Western | 2 | HFO | 341
2023-05-20 12:00 | Western | 6 | Coal | 2230
2023-05-20 12:00 | Western | 8 | HVDC | 911
2023-05-20 12:00 | Western | 11 | Solar | 351
2023-05-20 13:00 | Eastern | 1 | Gas | 4637
2023-05-20 13:00 | Eastern | 2 | HFO | 1129
2023-05-20 13:00 | Eastern | 3 | HSD | 95
2023-05-20 13:00 | Eastern | 5 | Hydro | 25
2023-05-20 13:00 | Eastern | 10 | Tripura | 164
2023-05-20 13:00 | Eastern | 11 | Solar | 99
2023-05-20 13:00 | Western | 1 | Gas | 965
2023-05-20 13:00 | Western | 2 | HFO | 364
2023-05-20 13:00 | Western | 6 | Coal | 2313
2023-05-20 13:00 | Western | 8 | HVDC | 912
2023-05-20 13:00 | Western | 11 | Solar | 275.29
2023-05-20 14:00 | Eastern | 1 | Gas | 4620
2023-05-20 14:00 | Eastern | 2 | HFO | 1201
2023-05-20 14:00 | Eastern | 3 | HSD | 340
2023-05-20 14:00 | Eastern | 5 | Hydro | 25
2023-05-20 14:00 | Eastern | 10 | Tripura | 162
2023-05-20 14:00 | Eastern | 11 | Solar | 86
2023-05-20 14:00 | Western | 1 | Gas | 972
2023-05-20 14:00 | Western | 2 | HFO | 389
2023-05-20 14:00 | Western | 6 | Coal | 2164
2023-05-20 14:00 | Western | 8 | HVDC | 912
2023-05-20 14:00 | Western | 11 | Solar | 257.66
2023-05-20 15:00 | Eastern | 1 | Gas | 4621
2023-05-20 15:00 | Eastern | 2 | HFO | 1195
2023-05-20 15:00 | Eastern | 3 | HSD | 141
2023-05-20 15:00 | Eastern | 5 | Hydro | 25
2023-05-20 15:00 | Eastern | 10 | Tripura | 164
2023-05-20 15:00 | Eastern | 11 | Solar | 70
2023-05-20 15:00 | Western | 1 | Gas | 930
2023-05-20 15:00 | Western | 2 | HFO | 399
2023-05-20 15:00 | Western | 6 | Coal | 2084
2023-05-20 15:00 | Western | 8 | HVDC | 912
2023-05-20 15:00 | Western | 11 | Solar | 246.61
2023-05-20 16:00 | Eastern | 1 | Gas | 4626
2023-05-20 16:00 | Eastern | 2 | HFO | 1222
2023-05-20 16:00 | Eastern | 5 | Hydro | 25
2023-05-20 16:00 | Eastern | 10 | Tripura | 136
2023-05-20 16:00 | Eastern | 11 | Solar | 46
2023-05-20 16:00 | Western | 1 | Gas | 969
2023-05-20 16:00 | Western | 2 | HFO | 399
2023-05-20 16:00 | Western | 6 | Coal | 2068
2023-05-20 16:00 | Western | 8 | HVDC | 912
2023-05-20 16:00 | Western | 11 | Solar | 147.46
2023-05-20 17:00 | Eastern | 1 | Gas | 4614
2023-05-20 17:00 | Eastern | 2 | HFO | 1302
2023-05-20 17:00 | Eastern | 5 | Hydro | 25
2023-05-20 17:00 | Eastern | 10 | Tripura | 126
2023-05-20 17:00 | Eastern | 11 | Solar | 22
2023-05-20 17:00 | Western | 1 | Gas | 954
2023-05-20 17:00 | Western | 2 | HFO | 437
2023-05-20 17:00 | Western | 6 | Coal | 2102
2023-05-20 17:00 | Western | 8 | HVDC | 913
2023-05-20 17:00 | Western | 11 | Solar | 75.05
2023-05-20 18:00 | Eastern | 1 | Gas | 4737
2023-05-20 18:00 | Eastern | 2 | HFO | 1550
2023-05-20 18:00 | Eastern | 5 | Hydro | 25
2023-05-20 18:00 | Eastern | 10 | Tripura | 150
2023-05-20 18:00 | Eastern | 11 | Solar | 4
2023-05-20 18:00 | Western | 1 | Gas | 907
2023-05-20 18:00 | Western | 2 | HFO | 519
2023-05-20 18:00 | Western | 3 | HSD | 0
2023-05-20 18:00 | Western | 6 | Coal | 2084
2023-05-20 18:00 | Western | 8 | HVDC | 914
2023-05-20 18:00 | Western | 11 | Solar | 18.23
2023-05-20 19:00 | Eastern | 1 | Gas | 4809
2023-05-20 19:00 | Eastern | 2 | HFO | 2401
2023-05-20 19:00 | Eastern | 3 | HSD | 390
2023-05-20 19:00 | Eastern | 5 | Hydro | 25
2023-05-20 19:00 | Eastern | 10 | Tripura | 146
2023-05-20 19:00 | Western | 1 | Gas | 895
2023-05-20 19:00 | Western | 2 | HFO | 844
2023-05-20 19:00 | Western | 3 | HSD | 0
2023-05-20 19:00 | Western | 6 | Coal | 2257
2023-05-20 19:00 | Western | 8 | HVDC | 914
2023-05-20 19:30 | Eastern | 1 | Gas | 4780
2023-05-20 19:30 | Eastern | 2 | HFO | 2564
2023-05-20 19:30 | Eastern | 3 | HSD | 248
2023-05-20 19:30 | Eastern | 5 | Hydro | 25
2023-05-20 19:30 | Eastern | 10 | Tripura | 146
2023-05-20 19:30 | Western | 1 | Gas | 890
2023-05-20 19:30 | Western | 2 | HFO | 993
2023-05-20 19:30 | Western | 3 | HSD | 0
2023-05-20 19:30 | Western | 6 | Coal | 2554
2023-05-20 19:30 | Western | 8 | HVDC | 779
2023-05-20 20:00 | Eastern | 1 | Gas | 4781
2023-05-20 20:00 | Eastern | 2 | HFO | 2610
2023-05-20 20:00 | Eastern | 3 | HSD | 255
2023-05-20 20:00 | Eastern | 5 | Hydro | 25
2023-05-20 20:00 | Eastern | 10 | Tripura | 140
2023-05-20 20:00 | Western | 1 | Gas | 889
2023-05-20 20:00 | Western | 2 | HFO | 1067
2023-05-20 20:00 | Western | 3 | HSD | 0
2023-05-20 20:00 | Western | 6 | Coal | 2573
2023-05-20 20:00 | Western | 8 | HVDC | 725
2023-05-20 21:00 | Eastern | 1 | Gas | 4893
2023-05-20 21:00 | Eastern | 2 | HFO | 2707
2023-05-20 21:00 | Eastern | 3 | HSD | 338
2023-05-20 21:00 | Eastern | 5 | Hydro | 25
2023-05-20 21:00 | Eastern | 10 | Tripura | 146
2023-05-20 21:00 | Western | 1 | Gas | 888
2023-05-20 21:00 | Western | 2 | HFO | 1094
2023-05-20 21:00 | Western | 3 | HSD | 0
2023-05-20 21:00 | Western | 6 | Coal | 2809
2023-05-20 21:00 | Western | 8 | HVDC | 726
2023-05-20 22:00 | Eastern | 1 | Gas | 4899
2023-05-20 22:00 | Eastern | 2 | HFO | 2504
2023-05-20 22:00 | Eastern | 3 | HSD | 330
2023-05-20 22:00 | Eastern | 5 | Hydro | 25
2023-05-20 22:00 | Eastern | 10 | Tripura | 150
2023-05-20 22:00 | Western | 1 | Gas | 871
2023-05-20 22:00 | Western | 2 | HFO | 1094
2023-05-20 22:00 | Western | 3 | HSD | 0
2023-05-20 22:00 | Western | 6 | Coal | 2814
2023-05-20 22:00 | Western | 8 | HVDC | 725
2023-05-20 23:00 | Eastern | 1 | Gas | 4999
2023-05-20 23:00 | Eastern | 2 | HFO | 1862
2023-05-20 23:00 | Eastern | 3 | HSD | 401
2023-05-20 23:00 | Eastern | 5 | Hydro | 0
2023-05-20 23:00 | Eastern | 10 | Tripura | 154
2023-05-20 23:00 | Western | 1 | Gas | 858
2023-05-20 23:00 | Western | 2 | HFO | 921
2023-05-20 23:00 | Western | 3 | HSD | 0
2023-05-20 23:00 | Western | 6 | Coal | 2814
2023-05-20 23:00 | Western | 8 | HVDC | 725
2023-05-21 | Eastern | 1 | Gas | 5011
2023-05-21 | Eastern | 2 | HFO | 1450
2023-05-21 | Eastern | 3 | HSD | 391
2023-05-21 | Eastern | 5 | Hydro | 0
2023-05-21 | Eastern | 10 | Tripura | 158
2023-05-21 | Eastern | 11 | Solar | 0
2023-05-21 | Western | 1 | Gas | 850
2023-05-21 | Western | 2 | HFO | 846
2023-05-21 | Western | 3 | HSD | 0
2023-05-21 | Western | 6 | Coal | 2813
2023-05-21 | Western | 8 | HVDC | 725
2023-05-21 01:00 | Eastern | 1 | Gas | 5014
2023-05-21 01:00 | Eastern | 2 | HFO | 1105
2023-05-21 01:00 | Eastern | 3 | HSD | 393
2023-05-21 01:00 | Eastern | 10 | Tripura | 162
2023-05-21 01:00 | Western | 1 | Gas | 845
2023-05-21 01:00 | Western | 2 | HFO | 684
2023-05-21 01:00 | Western | 3 | HSD | 0
2023-05-21 01:00 | Western | 6 | Coal | 2804
2023-05-21 01:00 | Western | 8 | HVDC | 803
2023-05-21 02:00 | Eastern | 1 | Gas | 4985
2023-05-21 02:00 | Eastern | 2 | HFO | 957
2023-05-21 02:00 | Eastern | 3 | HSD | 393
2023-05-21 02:00 | Eastern | 10 | Tripura | 162
2023-05-21 02:00 | Western | 1 | Gas | 857
2023-05-21 02:00 | Western | 2 | HFO | 653
2023-05-21 02:00 | Western | 3 | HSD | 0
2023-05-21 02:00 | Western | 6 | Coal | 2794
2023-05-21 02:00 | Western | 8 | HVDC | 727
2023-05-21 03:00 | Eastern | 1 | Gas | 4935
2023-05-21 03:00 | Eastern | 2 | HFO | 943
2023-05-21 03:00 | Eastern | 3 | HSD | 391
2023-05-21 03:00 | Eastern | 10 | Tripura | 156
2023-05-21 03:00 | Western | 1 | Gas | 862
2023-05-21 03:00 | Western | 2 | HFO | 610
2023-05-21 03:00 | Western | 3 | HSD | 0
2023-05-21 03:00 | Western | 6 | Coal | 2781
2023-05-21 03:00 | Western | 8 | HVDC | 918
2023-05-21 04:00 | Eastern | 1 | Gas | 4934
2023-05-21 04:00 | Eastern | 2 | HFO | 882
2023-05-21 04:00 | Eastern | 3 | HSD | 249
2023-05-21 04:00 | Eastern | 10 | Tripura | 152
2023-05-21 04:00 | Western | 1 | Gas | 860
2023-05-21 04:00 | Western | 2 | HFO | 610
2023-05-21 04:00 | Western | 3 | HSD | 0
2023-05-21 04:00 | Western | 6 | Coal | 2793
2023-05-21 04:00 | Western | 8 | HVDC | 918
2023-05-21 05:00 | Eastern | 1 | Gas | 4955
2023-05-21 05:00 | Eastern | 2 | HFO | 886
2023-05-21 05:00 | Eastern | 3 | HSD | 240
2023-05-21 05:00 | Eastern | 10 | Tripura | 152
2023-05-21 05:00 | Western | 1 | Gas | 860
2023-05-21 05:00 | Western | 2 | HFO | 404
2023-05-21 05:00 | Western | 3 | HSD | 0
2023-05-21 05:00 | Western | 6 | Coal | 2795
2023-05-21 05:00 | Western | 8 | HVDC | 918
2023-05-21 06:00 | Eastern | 1 | Gas | 5042
2023-05-21 06:00 | Eastern | 2 | HFO | 863
2023-05-21 06:00 | Eastern | 3 | HSD | 110
2023-05-21 06:00 | Eastern | 10 | Tripura | 138
2023-05-21 06:00 | Eastern | 11 | Solar | 3
2023-05-21 06:00 | Western | 1 | Gas | 851
2023-05-21 06:00 | Western | 2 | HFO | 278
2023-05-21 06:00 | Western | 3 | HSD | 0
2023-05-21 06:00 | Western | 6 | Coal | 2662
2023-05-21 06:00 | Western | 8 | HVDC | 918
2023-05-21 06:00 | Western | 11 | Solar | 7.34
2023-05-21 07:00 | Eastern | 1 | Gas | 4934
2023-05-21 07:00 | Eastern | 2 | HFO | 877
2023-05-21 07:00 | Eastern | 10 | Tripura | 140
2023-05-21 07:00 | Eastern | 11 | Solar | 12
2023-05-21 07:00 | Western | 1 | Gas | 848
2023-05-21 07:00 | Western | 2 | HFO | 313
2023-05-21 07:00 | Western | 3 | HSD | 0
2023-05-21 07:00 | Western | 6 | Coal | 2646
2023-05-21 07:00 | Western | 8 | HVDC | 918
2023-05-21 07:00 | Western | 11 | Solar | 26.85
2023-05-21 08:00 | Eastern | 1 | Gas | 4809
2023-05-21 08:00 | Eastern | 2 | HFO | 971
2023-05-21 08:00 | Eastern | 10 | Tripura | 136
2023-05-21 08:00 | Eastern | 11 | Solar | 26
2023-05-21 08:00 | Western | 1 | Gas | 823
2023-05-21 08:00 | Western | 2 | HFO | 353
2023-05-21 08:00 | Western | 3 | HSD | 0
2023-05-21 08:00 | Western | 6 | Coal | 2589
2023-05-21 08:00 | Western | 8 | HVDC | 918
2023-05-21 08:00 | Western | 11 | Solar | 145.44
2023-05-21 09:00 | Eastern | 1 | Gas | 4769
2023-05-21 09:00 | Eastern | 2 | HFO | 976
2023-05-21 09:00 | Eastern | 10 | Tripura | 142
2023-05-21 09:00 | Eastern | 11 | Solar | 47
2023-05-21 09:00 | Western | 1 | Gas | 794
2023-05-21 09:00 | Western | 2 | HFO | 347
2023-05-21 09:00 | Western | 3 | HSD | 6
2023-05-21 09:00 | Western | 6 | Coal | 2495
2023-05-21 09:00 | Western | 8 | HVDC | 917
2023-05-21 09:00 | Western | 11 | Solar | 134.44
2023-05-21 10:00 | Eastern | 1 | Gas | 4754
2023-05-21 10:00 | Eastern | 2 | HFO | 1164
2023-05-21 10:00 | Eastern | 3 | HSD | 140
2023-05-21 10:00 | Eastern | 5 | Hydro | 25
2023-05-21 10:00 | Eastern | 10 | Tripura | 146
2023-05-21 10:00 | Eastern | 11 | Solar | 84
2023-05-21 10:00 | Western | 1 | Gas | 778
2023-05-21 10:00 | Western | 2 | HFO | 363
2023-05-21 10:00 | Western | 3 | HSD | 40
2023-05-21 10:00 | Western | 6 | Coal | 2441
2023-05-21 10:00 | Western | 8 | HVDC | 918
2023-05-21 10:00 | Western | 11 | Solar | 177.24
2023-05-21 11:00 | Eastern | 1 | Gas | 4864
2023-05-21 11:00 | Eastern | 2 | HFO | 1306
2023-05-21 11:00 | Eastern | 3 | HSD | 245
2023-05-21 11:00 | Eastern | 5 | Hydro | 25
2023-05-21 11:00 | Eastern | 10 | Tripura | 154
2023-05-21 11:00 | Eastern | 11 | Solar | 71
2023-05-21 11:00 | Western | 1 | Gas | 777
2023-05-21 11:00 | Western | 2 | HFO | 450
2023-05-21 11:00 | Western | 3 | HSD | 49
2023-05-21 11:00 | Western | 6 | Coal | 2483
2023-05-21 11:00 | Western | 8 | HVDC | 918
2023-05-21 11:00 | Western | 11 | Solar | 142.24
2023-05-21 12:00 | Eastern | 1 | Gas | 4768
2023-05-21 12:00 | Eastern | 2 | HFO | 1342
2023-05-21 12:00 | Eastern | 3 | HSD | 390
2023-05-21 12:00 | Eastern | 5 | Hydro | 25
2023-05-21 12:00 | Eastern | 10 | Tripura | 160
2023-05-21 12:00 | Eastern | 11 | Solar | 97
2023-05-21 12:00 | Western | 1 | Gas | 775
2023-05-21 12:00 | Western | 2 | HFO | 454
2023-05-21 12:00 | Western | 3 | HSD | 156
2023-05-21 12:00 | Western | 6 | Coal | 2498
2023-05-21 12:00 | Western | 8 | HVDC | 918
2023-05-21 12:00 | Western | 11 | Solar | 212.89
2023-05-21 13:00 | Eastern | 1 | Gas | 4782
2023-05-21 13:00 | Eastern | 2 | HFO | 1440
2023-05-21 13:00 | Eastern | 3 | HSD | 385
2023-05-21 13:00 | Eastern | 5 | Hydro | 25
2023-05-21 13:00 | Eastern | 10 | Tripura | 170
2023-05-21 13:00 | Eastern | 11 | Solar | 98
2023-05-21 13:00 | Western | 1 | Gas | 756
2023-05-21 13:00 | Western | 2 | HFO | 462
2023-05-21 13:00 | Western | 3 | HSD | 270
2023-05-21 13:00 | Western | 6 | Coal | 2406
2023-05-21 13:00 | Western | 8 | HVDC | 918
2023-05-21 13:00 | Western | 11 | Solar | 164.29
2023-05-21 14:00 | Eastern | 1 | Gas | 4845
2023-05-21 14:00 | Eastern | 2 | HFO | 1402
2023-05-21 14:00 | Eastern | 3 | HSD | 184
2023-05-21 14:00 | Eastern | 5 | Hydro | 25
2023-05-21 14:00 | Eastern | 10 | Tripura | 170
2023-05-21 14:00 | Eastern | 11 | Solar | 76
2023-05-21 14:00 | Western | 1 | Gas | 735
2023-05-21 14:00 | Western | 2 | HFO | 481
2023-05-21 14:00 | Western | 3 | HSD | 281
2023-05-21 14:00 | Western | 6 | Coal | 2342
2023-05-21 14:00 | Western | 8 | HVDC | 919
2023-05-21 14:00 | Western | 11 | Solar | 284.95
2023-05-21 15:00 | Eastern | 1 | Gas | 4723
2023-05-21 15:00 | Eastern | 2 | HFO | 1298
2023-05-21 15:00 | Eastern | 3 | HSD | 191
2023-05-21 15:00 | Eastern | 5 | Hydro | 25
2023-05-21 15:00 | Eastern | 10 | Tripura | 178
2023-05-21 15:00 | Eastern | 11 | Solar | 75
2023-05-21 15:00 | Western | 1 | Gas | 733
2023-05-21 15:00 | Western | 2 | HFO | 477
2023-05-21 15:00 | Western | 3 | HSD | 0
2023-05-21 15:00 | Western | 6 | Coal | 2433
2023-05-21 15:00 | Western | 8 | HVDC | 917
2023-05-21 15:00 | Western | 11 | Solar | 204.67
2023-05-21 16:00 | Eastern | 1 | Gas | 4737
2023-05-21 16:00 | Eastern | 2 | HFO | 1268
2023-05-21 16:00 | Eastern | 3 | HSD | 0
2023-05-21 16:00 | Eastern | 5 | Hydro | 25
2023-05-21 16:00 | Eastern | 10 | Tripura | 168
2023-05-21 16:00 | Eastern | 11 | Solar | 30
2023-05-21 16:00 | Western | 1 | Gas | 731
2023-05-21 16:00 | Western | 2 | HFO | 474
2023-05-21 16:00 | Western | 3 | HSD | 15
2023-05-21 16:00 | Western | 6 | Coal | 2452
2023-05-21 16:00 | Western | 8 | HVDC | 917
2023-05-21 16:00 | Western | 11 | Solar | 119
2023-05-21 17:00 | Eastern | 1 | Gas | 4746
2023-05-21 17:00 | Eastern | 2 | HFO | 1263
2023-05-21 17:00 | Eastern | 5 | Hydro | 25
2023-05-21 17:00 | Eastern | 10 | Tripura | 162
2023-05-21 17:00 | Eastern | 11 | Solar | 28
2023-05-21 17:00 | Western | 1 | Gas | 741
2023-05-21 17:00 | Western | 2 | HFO | 505
2023-05-21 17:00 | Western | 3 | HSD | 12
2023-05-21 17:00 | Western | 6 | Coal | 2437
2023-05-21 17:00 | Western | 8 | HVDC | 917
2023-05-21 17:00 | Western | 11 | Solar | 50.02
2023-05-21 18:00 | Eastern | 1 | Gas | 4799
2023-05-21 18:00 | Eastern | 2 | HFO | 1603
2023-05-21 18:00 | Eastern | 3 | HSD | 0
2023-05-21 18:00 | Eastern | 5 | Hydro | 25
2023-05-21 18:00 | Eastern | 10 | Tripura | 164
2023-05-21 18:00 | Eastern | 11 | Solar | 2
2023-05-21 18:00 | Western | 1 | Gas | 760
2023-05-21 18:00 | Western | 2 | HFO | 579
2023-05-21 18:00 | Western | 3 | HSD | 12
2023-05-21 18:00 | Western | 6 | Coal | 2331
2023-05-21 18:00 | Western | 8 | HVDC | 918
2023-05-21 18:00 | Western | 11 | Solar | 17.03
2023-05-21 19:00 | Eastern | 1 | Gas | 4720
2023-05-21 19:00 | Eastern | 2 | HFO | 2467
2023-05-21 19:00 | Eastern | 3 | HSD | 233
2023-05-21 19:00 | Eastern | 5 | Hydro | 25
2023-05-21 19:00 | Eastern | 10 | Tripura | 170
2023-05-21 19:00 | Eastern | 11 | Solar | 0
2023-05-21 19:00 | Western | 1 | Gas | 779
2023-05-21 19:00 | Western | 2 | HFO | 740
2023-05-21 19:00 | Western | 3 | HSD | 15
2023-05-21 19:00 | Western | 6 | Coal | 2344
2023-05-21 19:00 | Western | 8 | HVDC | 918
2023-05-21 19:00 | Western | 11 | Solar | 0
2023-05-21 19:30 | Eastern | 1 | Gas | 4762
2023-05-21 19:30 | Eastern | 2 | HFO | 2525
2023-05-21 19:30 | Eastern | 3 | HSD | 129
2023-05-21 19:30 | Eastern | 5 | Hydro | 25
2023-05-21 19:30 | Eastern | 10 | Tripura | 156
2023-05-21 19:30 | Western | 1 | Gas | 777
2023-05-21 19:30 | Western | 2 | HFO | 783
2023-05-21 19:30 | Western | 3 | HSD | 15
2023-05-21 19:30 | Western | 6 | Coal | 2516
2023-05-21 19:30 | Western | 8 | HVDC | 845
2023-05-21 20:00 | Eastern | 1 | Gas | 4757
2023-05-21 20:00 | Eastern | 2 | HFO | 2565
2023-05-21 20:00 | Eastern | 3 | HSD | 0
2023-05-21 20:00 | Eastern | 5 | Hydro | 25
2023-05-21 20:00 | Eastern | 10 | Tripura | 164
2023-05-21 20:00 | Western | 1 | Gas | 800
2023-05-21 20:00 | Western | 2 | HFO | 792
2023-05-21 20:00 | Western | 3 | HSD | 0
2023-05-21 20:00 | Western | 6 | Coal | 2500
2023-05-21 20:00 | Western | 8 | HVDC | 775
2023-05-21 21:00 | Eastern | 1 | Gas | 4333
2023-05-21 21:00 | Eastern | 2 | HFO | 1699
2023-05-21 21:00 | Eastern | 5 | Hydro | 25
2023-05-21 21:00 | Eastern | 10 | Tripura | 156
2023-05-21 21:00 | Western | 1 | Gas | 721
2023-05-21 21:00 | Western | 2 | HFO | 134
2023-05-21 21:00 | Western | 3 | HSD | 0
2023-05-21 21:00 | Western | 6 | Coal | 2482
2023-05-21 21:00 | Western | 8 | HVDC | 822
2023-05-21 22:00 | Eastern | 1 | Gas | 4001
2023-05-21 22:00 | Eastern | 2 | HFO | 1068
2023-05-21 22:00 | Eastern | 5 | Hydro | 25
2023-05-21 22:00 | Eastern | 10 | Tripura | 160
2023-05-21 22:00 | Western | 1 | Gas | 709
2023-05-21 22:00 | Western | 2 | HFO | 101
2023-05-21 22:00 | Western | 3 | HSD | 0
2023-05-21 22:00 | Western | 6 | Coal | 2028
2023-05-21 22:00 | Western | 8 | HVDC | 822
2023-05-21 23:00 | Eastern | 1 | Gas | 4221
2023-05-21 23:00 | Eastern | 2 | HFO | 1024
2023-05-21 23:00 | Eastern | 10 | Tripura | 28
2023-05-21 23:00 | Western | 1 | Gas | 754
2023-05-21 23:00 | Western | 2 | HFO | 86
2023-05-21 23:00 | Western | 3 | HSD | 0
2023-05-21 23:00 | Western | 6 | Coal | 2096
2023-05-21 23:00 | Western | 8 | HVDC | 824
2023-05-22 | Eastern | 1 | Gas | 4483
2023-05-22 | Eastern | 2 | HFO | 886
2023-05-22 | Eastern | 3 | HSD | 0
2023-05-22 | Eastern | 10 | Tripura | 76
2023-05-22 | Eastern | 11 | Solar | 0
2023-05-22 | Western | 1 | Gas | 724
2023-05-22 | Western | 2 | HFO | 34
2023-05-22 | Western | 3 | HSD | 0
2023-05-22 | Western | 6 | Coal | 2150
2023-05-22 | Western | 8 | HVDC | 823
2023-05-22 | Western | 11 | Solar | 0
2023-05-22 01:00 | Eastern | 1 | Gas | 4424
2023-05-22 01:00 | Eastern | 2 | HFO | 800
2023-05-22 01:00 | Eastern | 10 | Tripura | 102
2023-05-22 01:00 | Western | 1 | Gas | 735
2023-05-22 01:00 | Western | 2 | HFO | 34
2023-05-22 01:00 | Western | 3 | HSD | 0
2023-05-22 01:00 | Western | 6 | Coal | 2156
2023-05-22 01:00 | Western | 8 | HVDC | 921
2023-05-22 02:00 | Eastern | 1 | Gas | 4491.5
2023-05-22 02:00 | Eastern | 2 | HFO | 736
2023-05-22 02:00 | Eastern | 10 | Tripura | 118
2023-05-22 02:00 | Western | 1 | Gas | 743
2023-05-22 02:00 | Western | 2 | HFO | 34
2023-05-22 02:00 | Western | 3 | HSD | 0
2023-05-22 02:00 | Western | 6 | Coal | 2150
2023-05-22 02:00 | Western | 8 | HVDC | 920
2023-05-22 03:00 | Eastern | 1 | Gas | 4430
2023-05-22 03:00 | Eastern | 2 | HFO | 751
2023-05-22 03:00 | Eastern | 10 | Tripura | 88
2023-05-22 03:00 | Western | 1 | Gas | 812
2023-05-22 03:00 | Western | 2 | HFO | 34
2023-05-22 03:00 | Western | 3 | HSD | 0
2023-05-22 03:00 | Western | 6 | Coal | 2144
2023-05-22 03:00 | Western | 8 | HVDC | 920
2023-05-22 04:00 | Eastern | 1 | Gas | 4491
2023-05-22 04:00 | Eastern | 2 | HFO | 679
2023-05-22 04:00 | Eastern | 10 | Tripura | 94
2023-05-22 04:00 | Western | 1 | Gas | 816
2023-05-22 04:00 | Western | 2 | HFO | 34
2023-05-22 04:00 | Western | 3 | HSD | 0
2023-05-22 04:00 | Western | 6 | Coal | 2142
2023-05-22 04:00 | Western | 8 | HVDC | 922
2023-05-22 05:00 | Eastern | 1 | Gas | 4482
2023-05-22 05:00 | Eastern | 2 | HFO | 687
2023-05-22 05:00 | Eastern | 10 | Tripura | 102
2023-05-22 05:00 | Western | 1 | Gas | 814
2023-05-22 05:00 | Western | 3 | HSD | 0
2023-05-22 05:00 | Western | 6 | Coal | 2081
2023-05-22 05:00 | Western | 8 | HVDC | 921
2023-05-22 06:00 | Eastern | 1 | Gas | 4433
2023-05-22 06:00 | Eastern | 2 | HFO | 587
2023-05-22 06:00 | Eastern | 10 | Tripura | 100
2023-05-22 06:00 | Eastern | 11 | Solar | 5
2023-05-22 06:00 | Western | 1 | Gas | 795
2023-05-22 06:00 | Western | 3 | HSD | 0
2023-05-22 06:00 | Western | 6 | Coal | 2009
2023-05-22 06:00 | Western | 8 | HVDC | 920
2023-05-22 06:00 | Western | 11 | Solar | 14.34
2023-05-22 07:00 | Eastern | 1 | Gas | 4506
2023-05-22 07:00 | Eastern | 2 | HFO | 582
2023-05-22 07:00 | Eastern | 10 | Tripura | 108
2023-05-22 07:00 | Eastern | 11 | Solar | 23
2023-05-22 07:00 | Western | 1 | Gas | 795
2023-05-22 07:00 | Western | 3 | HSD | 0
2023-05-22 07:00 | Western | 6 | Coal | 2013
2023-05-22 07:00 | Western | 8 | HVDC | 922
2023-05-22 07:00 | Western | 11 | Solar | 58.1
2023-05-22 08:00 | Eastern | 1 | Gas | 4489
2023-05-22 08:00 | Eastern | 2 | HFO | 622
2023-05-22 08:00 | Eastern | 10 | Tripura | 112
2023-05-22 08:00 | Eastern | 11 | Solar | 43
2023-05-22 08:00 | Western | 1 | Gas | 873
2023-05-22 08:00 | Western | 2 | HFO | 1
2023-05-22 08:00 | Western | 3 | HSD | 0
2023-05-22 08:00 | Western | 6 | Coal | 2116
2023-05-22 08:00 | Western | 8 | HVDC | 921
2023-05-22 08:00 | Western | 11 | Solar | 90.38
2023-05-22 09:00 | Eastern | 1 | Gas | 4848.5
2023-05-22 09:00 | Eastern | 2 | HFO | 771
2023-05-22 09:00 | Eastern | 10 | Tripura | 126
2023-05-22 09:00 | Eastern | 11 | Solar | 59
2023-05-22 09:00 | Western | 1 | Gas | 911
2023-05-22 09:00 | Western | 2 | HFO | 65
2023-05-22 09:00 | Western | 3 | HSD | 0
2023-05-22 09:00 | Western | 6 | Coal | 2181
2023-05-22 09:00 | Western | 8 | HVDC | 921
2023-05-22 09:00 | Western | 11 | Solar | 166.63
2023-05-22 10:00 | Eastern | 1 | Gas | 5194
2023-05-22 10:00 | Eastern | 2 | HFO | 868
2023-05-22 10:00 | Eastern | 5 | Hydro | 0
2023-05-22 10:00 | Eastern | 10 | Tripura | 140
2023-05-22 10:00 | Eastern | 11 | Solar | 97
2023-05-22 10:00 | Western | 1 | Gas | 902
2023-05-22 10:00 | Western | 2 | HFO | 87
2023-05-22 10:00 | Western | 3 | HSD | 0
2023-05-22 10:00 | Western | 6 | Coal | 2224
2023-05-22 10:00 | Western | 8 | HVDC | 921
2023-05-22 10:00 | Western | 11 | Solar | 172.43
2023-05-22 11:00 | Eastern | 1 | Gas | 5143
2023-05-22 11:00 | Eastern | 2 | HFO | 1148
2023-05-22 11:00 | Eastern | 5 | Hydro | 25
2023-05-22 11:00 | Eastern | 10 | Tripura | 148
2023-05-22 11:00 | Eastern | 11 | Solar | 107
2023-05-22 11:00 | Western | 1 | Gas | 957
2023-05-22 11:00 | Western | 2 | HFO | 92
2023-05-22 11:00 | Western | 3 | HSD | 0
2023-05-22 11:00 | Western | 6 | Coal | 2317
2023-05-22 11:00 | Western | 8 | HVDC | 921
2023-05-22 11:00 | Western | 11 | Solar | 227.68
2023-05-22 12:00 | Eastern | 1 | Gas | 5263.79
2023-05-22 12:00 | Eastern | 2 | HFO | 1212
2023-05-22 12:00 | Eastern | 3 | HSD | 223
2023-05-22 12:00 | Eastern | 5 | Hydro | 25
2023-05-22 12:00 | Eastern | 10 | Tripura | 150
2023-05-22 12:00 | Eastern | 11 | Solar | 83
2023-05-22 12:00 | Western | 1 | Gas | 989
2023-05-22 12:00 | Western | 2 | HFO | 219
2023-05-22 12:00 | Western | 3 | HSD | 0
2023-05-22 12:00 | Western | 6 | Coal | 2415
2023-05-22 12:00 | Western | 8 | HVDC | 921
2023-05-22 12:00 | Western | 11 | Solar | 250.09
2023-05-22 13:00 | Eastern | 1 | Gas | 5224.79
2023-05-22 13:00 | Eastern | 2 | HFO | 1223
2023-05-22 13:00 | Eastern | 3 | HSD | 389
2023-05-22 13:00 | Eastern | 5 | Hydro | 25
2023-05-22 13:00 | Eastern | 10 | Tripura | 160
2023-05-22 13:00 | Eastern | 11 | Solar | 84
2023-05-22 13:00 | Western | 1 | Gas | 984
2023-05-22 13:00 | Western | 2 | HFO | 293
2023-05-22 13:00 | Western | 3 | HSD | 0
2023-05-22 13:00 | Western | 6 | Coal | 2500
2023-05-22 13:00 | Western | 8 | HVDC | 922
2023-05-22 13:00 | Western | 11 | Solar | 330.78
2023-05-22 14:00 | Eastern | 1 | Gas | 5373.79
2023-05-22 14:00 | Eastern | 2 | HFO | 1218
2023-05-22 14:00 | Eastern | 3 | HSD | 240
2023-05-22 14:00 | Eastern | 5 | Hydro | 25
2023-05-22 14:00 | Eastern | 10 | Tripura | 158
2023-05-22 14:00 | Eastern | 11 | Solar | 80
2023-05-22 14:00 | Western | 1 | Gas | 940
2023-05-22 14:00 | Western | 2 | HFO | 303
2023-05-22 14:00 | Western | 3 | HSD | 0
2023-05-22 14:00 | Western | 6 | Coal | 2493
2023-05-22 14:00 | Western | 8 | HVDC | 921
2023-05-22 14:00 | Western | 11 | Solar | 277.39
2023-05-22 15:00 | Eastern | 1 | Gas | 5266.79
2023-05-22 15:00 | Eastern | 2 | HFO | 1130
2023-05-22 15:00 | Eastern | 3 | HSD | 438
2023-05-22 15:00 | Eastern | 5 | Hydro | 25
2023-05-22 15:00 | Eastern | 10 | Tripura | 170
2023-05-22 15:00 | Eastern | 11 | Solar | 69
2023-05-22 15:00 | Western | 1 | Gas | 932
2023-05-22 15:00 | Western | 2 | HFO | 318
2023-05-22 15:00 | Western | 3 | HSD | 0
2023-05-22 15:00 | Western | 6 | Coal | 2550
2023-05-22 15:00 | Western | 8 | HVDC | 921
2023-05-22 15:00 | Western | 11 | Solar | 228.34
2023-05-22 16:00 | Eastern | 1 | Gas | 5352.79
2023-05-22 16:00 | Eastern | 2 | HFO | 1177
2023-05-22 16:00 | Eastern | 3 | HSD | 440
2023-05-22 16:00 | Eastern | 5 | Hydro | 25
2023-05-22 16:00 | Eastern | 10 | Tripura | 162
2023-05-22 16:00 | Eastern | 11 | Solar | 43
2023-05-22 16:00 | Western | 1 | Gas | 992
2023-05-22 16:00 | Western | 2 | HFO | 350
2023-05-22 16:00 | Western | 3 | HSD | 0
2023-05-22 16:00 | Western | 6 | Coal | 2550
2023-05-22 16:00 | Western | 8 | HVDC | 906
2023-05-22 16:00 | Western | 11 | Solar | 155.2
2023-05-22 17:00 | Eastern | 1 | Gas | 5226.79
2023-05-22 17:00 | Eastern | 2 | HFO | 1279
2023-05-22 17:00 | Eastern | 3 | HSD | 434
2023-05-22 17:00 | Eastern | 5 | Hydro | 25
2023-05-22 17:00 | Eastern | 10 | Tripura | 148
2023-05-22 17:00 | Eastern | 11 | Solar | 17
2023-05-22 17:00 | Western | 1 | Gas | 994
2023-05-22 17:00 | Western | 2 | HFO | 394
2023-05-22 17:00 | Western | 3 | HSD | 0
2023-05-22 17:00 | Western | 6 | Coal | 2553
2023-05-22 17:00 | Western | 8 | HVDC | 906
2023-05-22 17:00 | Western | 11 | Solar | 76.88
2023-05-22 18:00 | Eastern | 1 | Gas | 5248.79
2023-05-22 18:00 | Eastern | 2 | HFO | 1714
2023-05-22 18:00 | Eastern | 3 | HSD | 50
2023-05-22 18:00 | Eastern | 5 | Hydro | 25
2023-05-22 18:00 | Eastern | 10 | Tripura | 150
2023-05-22 18:00 | Eastern | 11 | Solar | 3
2023-05-22 18:00 | Western | 1 | Gas | 1003
2023-05-22 18:00 | Western | 2 | HFO | 444
2023-05-22 18:00 | Western | 3 | HSD | 0
2023-05-22 18:00 | Western | 6 | Coal | 2488
2023-05-22 18:00 | Western | 8 | HVDC | 906
2023-05-22 18:00 | Western | 11 | Solar | 18.17
2023-05-22 19:00 | Eastern | 1 | Gas | 5361.79
2023-05-22 19:00 | Eastern | 2 | HFO | 2531
2023-05-22 19:00 | Eastern | 3 | HSD | 220
2023-05-22 19:00 | Eastern | 5 | Hydro | 25
2023-05-22 19:00 | Eastern | 10 | Tripura | 148
2023-05-22 19:00 | Eastern | 11 | Solar | 0
2023-05-22 19:00 | Western | 1 | Gas | 982
2023-05-22 19:00 | Western | 2 | HFO | 718
2023-05-22 19:00 | Western | 3 | HSD | 0
2023-05-22 19:00 | Western | 6 | Coal | 2501
2023-05-22 19:00 | Western | 8 | HVDC | 906
2023-05-22 19:00 | Western | 11 | Solar | 0
2023-05-22 19:30 | Eastern | 1 | Gas | 5269.79
2023-05-22 19:30 | Eastern | 2 | HFO | 2657
2023-05-22 19:30 | Eastern | 3 | HSD | 61
2023-05-22 19:30 | Eastern | 5 | Hydro | 25
2023-05-22 19:30 | Eastern | 10 | Tripura | 142
2023-05-22 19:30 | Western | 1 | Gas | 1030
2023-05-22 19:30 | Western | 2 | HFO | 837
2023-05-22 19:30 | Western | 3 | HSD | 0
2023-05-22 19:30 | Western | 6 | Coal | 2627
2023-05-22 19:30 | Western | 8 | HVDC | 905
2023-05-22 20:00 | Eastern | 1 | Gas | 5327.79
2023-05-22 20:00 | Eastern | 2 | HFO | 2706
2023-05-22 20:00 | Eastern | 3 | HSD | 62
2023-05-22 20:00 | Eastern | 5 | Hydro | 25
2023-05-22 20:00 | Eastern | 10 | Tripura | 158
2023-05-22 20:00 | Western | 1 | Gas | 1025
2023-05-22 20:00 | Western | 2 | HFO | 832
2023-05-22 20:00 | Western | 3 | HSD | 0
2023-05-22 20:00 | Western | 6 | Coal | 2730
2023-05-22 20:00 | Western | 8 | HVDC | 795
2023-05-22 21:00 | Eastern | 1 | Gas | 5387.79
2023-05-22 21:00 | Eastern | 2 | HFO | 2787
2023-05-22 21:00 | Eastern | 3 | HSD | 62
2023-05-22 21:00 | Eastern | 5 | Hydro | 25
2023-05-22 21:00 | Eastern | 10 | Tripura | 144
2023-05-22 21:00 | Western | 1 | Gas | 1028
2023-05-22 21:00 | Western | 2 | HFO | 887
2023-05-22 21:00 | Western | 3 | HSD | 0
2023-05-22 21:00 | Western | 6 | Coal | 2822
2023-05-22 21:00 | Western | 8 | HVDC | 795
2023-05-22 22:00 | Eastern | 1 | Gas | 5370.79
2023-05-22 22:00 | Eastern | 2 | HFO | 2568
2023-05-22 22:00 | Eastern | 3 | HSD | 62
2023-05-22 22:00 | Eastern | 5 | Hydro | 25
2023-05-22 22:00 | Eastern | 10 | Tripura | 154
2023-05-22 22:00 | Western | 1 | Gas | 1031
2023-05-22 22:00 | Western | 2 | HFO | 1002
2023-05-22 22:00 | Western | 3 | HSD | 0
2023-05-22 22:00 | Western | 6 | Coal | 2816
2023-05-22 22:00 | Western | 8 | HVDC | 765
2023-05-22 23:00 | Eastern | 1 | Gas | 5399.79
2023-05-22 23:00 | Eastern | 2 | HFO | 1982
2023-05-22 23:00 | Eastern | 3 | HSD | 363
2023-05-22 23:00 | Eastern | 5 | Hydro | 0
2023-05-22 23:00 | Eastern | 10 | Tripura | 152
2023-05-22 23:00 | Western | 1 | Gas | 1033
2023-05-22 23:00 | Western | 2 | HFO | 886
2023-05-22 23:00 | Western | 3 | HSD | 0
2023-05-22 23:00 | Western | 6 | Coal | 2824
2023-05-22 23:00 | Western | 8 | HVDC | 766
2023-05-23 | Eastern | 1 | Gas | 5497.79
2023-05-23 | Eastern | 2 | HFO | 1585
2023-05-23 | Eastern | 3 | HSD | 367
2023-05-23 | Eastern | 10 | Tripura | 156
2023-05-23 | Western | 1 | Gas | 1006
2023-05-23 | Western | 2 | HFO | 850
2023-05-23 | Western | 3 | HSD | 0
2023-05-23 | Western | 6 | Coal | 2826
2023-05-23 | Western | 8 | HVDC | 765
2023-05-23 01:00 | Eastern | 1 | Gas | 5419.79
2023-05-23 01:00 | Eastern | 2 | HFO | 1213
2023-05-23 01:00 | Eastern | 3 | HSD | 415
2023-05-23 01:00 | Eastern | 10 | Tripura | 150
2023-05-23 01:00 | Western | 1 | Gas | 1008
2023-05-23 01:00 | Western | 2 | HFO | 772
2023-05-23 01:00 | Western | 3 | HSD | 0
2023-05-23 01:00 | Western | 6 | Coal | 2821
2023-05-23 01:00 | Western | 8 | HVDC | 811
2023-05-23 02:00 | Eastern | 1 | Gas | 5429.79
2023-05-23 02:00 | Eastern | 2 | HFO | 1149
2023-05-23 02:00 | Eastern | 3 | HSD | 368
2023-05-23 02:00 | Eastern | 10 | Tripura | 148
2023-05-23 02:00 | Western | 1 | Gas | 1009
2023-05-23 02:00 | Western | 2 | HFO | 780
2023-05-23 02:00 | Western | 3 | HSD | 0
2023-05-23 02:00 | Western | 6 | Coal | 2819
2023-05-23 02:00 | Western | 8 | HVDC | 811
2023-05-23 03:00 | Eastern | 1 | Gas | 5425.79
2023-05-23 03:00 | Eastern | 2 | HFO | 1134
2023-05-23 03:00 | Eastern | 3 | HSD | 172
2023-05-23 03:00 | Eastern | 10 | Tripura | 148
2023-05-23 03:00 | Western | 1 | Gas | 1045
2023-05-23 03:00 | Western | 2 | HFO | 602
2023-05-23 03:00 | Western | 3 | HSD | 0
2023-05-23 03:00 | Western | 6 | Coal | 2816
2023-05-23 03:00 | Western | 8 | HVDC | 906
2023-05-23 04:00 | Eastern | 1 | Gas | 5452.79
2023-05-23 04:00 | Eastern | 2 | HFO | 1117
2023-05-23 04:00 | Eastern | 10 | Tripura | 152
2023-05-23 04:00 | Western | 1 | Gas | 1044
2023-05-23 04:00 | Western | 2 | HFO | 508
2023-05-23 04:00 | Western | 3 | HSD | 0
2023-05-23 04:00 | Western | 6 | Coal | 2819
2023-05-23 04:00 | Western | 8 | HVDC | 907
2023-05-23 05:00 | Eastern | 1 | Gas | 5401.79
2023-05-23 05:00 | Eastern | 2 | HFO | 1117
2023-05-23 05:00 | Eastern | 10 | Tripura | 144
2023-05-23 05:00 | Western | 1 | Gas | 1053
2023-05-23 05:00 | Western | 2 | HFO | 447
2023-05-23 05:00 | Western | 6 | Coal | 2825
2023-05-23 05:00 | Western | 8 | HVDC | 906
2023-05-23 06:00 | Eastern | 1 | Gas | 5325.79
2023-05-23 06:00 | Eastern | 2 | HFO | 1039
2023-05-23 06:00 | Eastern | 10 | Tripura | 148
2023-05-23 06:00 | Eastern | 11 | Solar | 5
2023-05-23 06:00 | Western | 1 | Gas | 967
2023-05-23 06:00 | Western | 2 | HFO | 337
2023-05-23 06:00 | Western | 6 | Coal | 2643
2023-05-23 06:00 | Western | 8 | HVDC | 906
2023-05-23 06:00 | Western | 11 | Solar | 14.09
2023-05-23 07:00 | Eastern | 1 | Gas | 5234.79
2023-05-23 07:00 | Eastern | 2 | HFO | 982
2023-05-23 07:00 | Eastern | 10 | Tripura | 138
2023-05-23 07:00 | Eastern | 11 | Solar | 21
2023-05-23 07:00 | Western | 1 | Gas | 969
2023-05-23 07:00 | Western | 2 | HFO | 372
2023-05-23 07:00 | Western | 6 | Coal | 2620
2023-05-23 07:00 | Western | 8 | HVDC | 908
2023-05-23 07:00 | Western | 11 | Solar | 55.32
2023-05-23 08:00 | Eastern | 1 | Gas | 5226.79
2023-05-23 08:00 | Eastern | 2 | HFO | 952
2023-05-23 08:00 | Eastern | 10 | Tripura | 134
2023-05-23 08:00 | Eastern | 11 | Solar | 49
2023-05-23 08:00 | Western | 1 | Gas | 975
2023-05-23 08:00 | Western | 2 | HFO | 388
2023-05-23 08:00 | Western | 6 | Coal | 2562
2023-05-23 08:00 | Western | 8 | HVDC | 906
2023-05-23 08:00 | Western | 11 | Solar | 122.79
2023-05-23 09:00 | Eastern | 1 | Gas | 5307.79
2023-05-23 09:00 | Eastern | 2 | HFO | 956
2023-05-23 09:00 | Eastern | 10 | Tripura | 140
2023-05-23 09:00 | Eastern | 11 | Solar | 54
2023-05-23 09:00 | Western | 1 | Gas | 1082
2023-05-23 09:00 | Western | 2 | HFO | 357
2023-05-23 09:00 | Western | 6 | Coal | 2460
2023-05-23 09:00 | Western | 8 | HVDC | 907
2023-05-23 09:00 | Western | 11 | Solar | 156.13
2023-05-23 10:00 | Eastern | 1 | Gas | 5325.79
2023-05-23 10:00 | Eastern | 2 | HFO | 1173
2023-05-23 10:00 | Eastern | 5 | Hydro | 25
2023-05-23 10:00 | Eastern | 10 | Tripura | 146
2023-05-23 10:00 | Eastern | 11 | Solar | 92
2023-05-23 10:00 | Western | 1 | Gas | 1211
2023-05-23 10:00 | Western | 2 | HFO | 318
2023-05-23 10:00 | Western | 6 | Coal | 2381
2023-05-23 10:00 | Western | 8 | HVDC | 906
2023-05-23 10:00 | Western | 11 | Solar | 192.5
2023-05-23 11:00 | Eastern | 1 | Gas | 5155.79
2023-05-23 11:00 | Eastern | 2 | HFO | 1235
2023-05-23 11:00 | Eastern | 3 | HSD | 106
2023-05-23 11:00 | Eastern | 5 | Hydro | 25
2023-05-23 11:00 | Eastern | 10 | Tripura | 148
2023-05-23 11:00 | Eastern | 11 | Solar | 47
2023-05-23 11:00 | Western | 1 | Gas | 1341
2023-05-23 11:00 | Western | 2 | HFO | 294
2023-05-23 11:00 | Western | 6 | Coal | 2360
2023-05-23 11:00 | Western | 8 | HVDC | 907
2023-05-23 11:00 | Western | 11 | Solar | 213
2023-05-23 12:00 | Eastern | 1 | Gas | 5108.79
2023-05-23 12:00 | Eastern | 2 | HFO | 1347
2023-05-23 12:00 | Eastern | 3 | HSD | 212
2023-05-23 12:00 | Eastern | 5 | Hydro | 25
2023-05-23 12:00 | Eastern | 10 | Tripura | 164
2023-05-23 12:00 | Eastern | 11 | Solar | 64
2023-05-23 12:00 | Western | 1 | Gas | 1368
2023-05-23 12:00 | Western | 2 | HFO | 285
2023-05-23 12:00 | Western | 6 | Coal | 2431
2023-05-23 12:00 | Western | 8 | HVDC | 907
2023-05-23 12:00 | Western | 11 | Solar | 310.89
2023-05-23 13:00 | Eastern | 1 | Gas | 5038.79
2023-05-23 13:00 | Eastern | 2 | HFO | 1375
2023-05-23 13:00 | Eastern | 3 | HSD | 110
2023-05-23 13:00 | Eastern | 5 | Hydro | 25
2023-05-23 13:00 | Eastern | 10 | Tripura | 162
2023-05-23 13:00 | Eastern | 11 | Solar | 102
2023-05-23 13:00 | Western | 1 | Gas | 1370
2023-05-23 13:00 | Western | 2 | HFO | 278
2023-05-23 13:00 | Western | 6 | Coal | 2462
2023-05-23 13:00 | Western | 8 | HVDC | 906
2023-05-23 13:00 | Western | 11 | Solar | 278.64
2023-05-23 14:00 | Eastern | 1 | Gas | 4661.79
2023-05-23 14:00 | Eastern | 2 | HFO | 1221
2023-05-23 14:00 | Eastern | 5 | Hydro | 25
2023-05-23 14:00 | Eastern | 10 | Tripura | 60
2023-05-23 14:00 | Eastern | 11 | Solar | 81
2023-05-23 14:00 | Western | 1 | Gas | 1126
2023-05-23 14:00 | Western | 2 | HFO | 208
2023-05-23 14:00 | Western | 6 | Coal | 2273
2023-05-23 14:00 | Western | 8 | HVDC | 907
2023-05-23 14:00 | Western | 11 | Solar | 143.35
2023-05-23 15:00 | Eastern | 1 | Gas | 4645
2023-05-23 15:00 | Eastern | 2 | HFO | 1199
2023-05-23 15:00 | Eastern | 5 | Hydro | 25
2023-05-23 15:00 | Eastern | 10 | Tripura | 74
2023-05-23 15:00 | Eastern | 11 | Solar | 57
2023-05-23 15:00 | Western | 1 | Gas | 1047
2023-05-23 15:00 | Western | 2 | HFO | 113
2023-05-23 15:00 | Western | 6 | Coal | 2197
2023-05-23 15:00 | Western | 8 | HVDC | 907
2023-05-23 15:00 | Western | 11 | Solar | 66.53
2023-05-23 16:00 | Eastern | 1 | Gas | 4711
2023-05-23 16:00 | Eastern | 2 | HFO | 884
2023-05-23 16:00 | Eastern | 5 | Hydro | 25
2023-05-23 16:00 | Eastern | 10 | Tripura | 80
2023-05-23 16:00 | Eastern | 11 | Solar | 26
2023-05-23 16:00 | Western | 1 | Gas | 794
2023-05-23 16:00 | Western | 2 | HFO | 10
2023-05-23 16:00 | Western | 6 | Coal | 1966
2023-05-23 16:00 | Western | 8 | HVDC | 907
2023-05-23 16:00 | Western | 11 | Solar | 44
2023-05-23 17:00 | Eastern | 1 | Gas | 4554
2023-05-23 17:00 | Eastern | 2 | HFO | 786
2023-05-23 17:00 | Eastern | 5 | Hydro | 25
2023-05-23 17:00 | Eastern | 10 | Tripura | 96
2023-05-23 17:00 | Eastern | 11 | Solar | 3
2023-05-23 17:00 | Western | 1 | Gas | 760
2023-05-23 17:00 | Western | 6 | Coal | 1663
2023-05-23 17:00 | Western | 8 | HVDC | 805
2023-05-23 17:00 | Western | 11 | Solar | 15
2023-05-23 18:00 | Eastern | 1 | Gas | 3100
2023-05-23 18:00 | Eastern | 2 | HFO | 535
2023-05-23 18:00 | Eastern | 5 | Hydro | 25
2023-05-23 18:00 | Eastern | 10 | Tripura | 112
2023-05-23 18:00 | Eastern | 11 | Solar | 0
2023-05-23 18:00 | Western | 1 | Gas | 740
2023-05-23 18:00 | Western | 6 | Coal | 1652
2023-05-23 18:00 | Western | 8 | HVDC | 301
2023-05-23 18:00 | Western | 11 | Solar | 2
2023-05-23 19:00 | Eastern | 1 | Gas | 3095
2023-05-23 19:00 | Eastern | 2 | HFO | 678
2023-05-23 19:00 | Eastern | 5 | Hydro | 25
2023-05-23 19:00 | Eastern | 10 | Tripura | 94
2023-05-23 19:00 | Western | 1 | Gas | 772
2023-05-23 19:00 | Western | 6 | Coal | 1632
2023-05-23 19:00 | Western | 8 | HVDC | 351
2023-05-23 19:30 | Eastern | 1 | Gas | 3351
2023-05-23 19:30 | Eastern | 2 | HFO | 655
2023-05-23 19:30 | Eastern | 5 | Hydro | 25
2023-05-23 19:30 | Eastern | 10 | Tripura | 100
2023-05-23 19:30 | Western | 1 | Gas | 755
2023-05-23 19:30 | Western | 6 | Coal | 1634
2023-05-23 19:30 | Western | 8 | HVDC | 546
2023-05-23 20:00 | Eastern | 1 | Gas | 3535
2023-05-23 20:00 | Eastern | 2 | HFO | 673
2023-05-23 20:00 | Eastern | 5 | Hydro | 25
2023-05-23 20:00 | Eastern | 10 | Tripura | 108
2023-05-23 20:00 | Western | 1 | Gas | 785
2023-05-23 20:00 | Western | 6 | Coal | 1657
2023-05-23 20:00 | Western | 8 | HVDC | 825
2023-05-23 21:00 | Eastern | 1 | Gas | 4261
2023-05-23 21:00 | Eastern | 2 | HFO | 665
2023-05-23 21:00 | Eastern | 5 | Hydro | 25
2023-05-23 21:00 | Eastern | 10 | Tripura | 124
2023-05-23 21:00 | Western | 1 | Gas | 821
2023-05-23 21:00 | Western | 6 | Coal | 1616
2023-05-23 21:00 | Western | 8 | HVDC | 834
2023-05-23 22:00 | Eastern | 1 | Gas | 4617
2023-05-23 22:00 | Eastern | 2 | HFO | 682
2023-05-23 22:00 | Eastern | 5 | Hydro | 25
2023-05-23 22:00 | Eastern | 10 | Tripura | 136
2023-05-23 22:00 | Western | 1 | Gas | 926
2023-05-23 22:00 | Western | 6 | Coal | 1614
2023-05-23 22:00 | Western | 8 | HVDC | 799
2023-05-23 23:00 | Eastern | 1 | Gas | 4674
2023-05-23 23:00 | Eastern | 2 | HFO | 605
2023-05-23 23:00 | Eastern | 5 | Hydro | 0
2023-05-23 23:00 | Eastern | 10 | Tripura | 120
2023-05-23 23:00 | Western | 1 | Gas | 935
2023-05-23 23:00 | Western | 6 | Coal | 1627
2023-05-23 23:00 | Western | 8 | HVDC | 799
2023-05-24 | Eastern | 1 | Gas | 4917
2023-05-24 | Eastern | 2 | HFO | 575
2023-05-24 | Eastern | 3 | HSD | 0
2023-05-24 | Eastern | 10 | Tripura | 112
2023-05-24 | Western | 1 | Gas | 962
2023-05-24 | Western | 2 | HFO | 0
2023-05-24 | Western | 6 | Coal | 1641
2023-05-24 | Western | 8 | HVDC | 799
2023-05-24 01:00 | Eastern | 1 | Gas | 4885
2023-05-24 01:00 | Eastern | 2 | HFO | 508
2023-05-24 01:00 | Eastern | 10 | Tripura | 108
2023-05-24 01:00 | Western | 1 | Gas | 992
2023-05-24 01:00 | Western | 6 | Coal | 1625
2023-05-24 01:00 | Western | 8 | HVDC | 837
2023-05-24 02:00 | Eastern | 1 | Gas | 4757
2023-05-24 02:00 | Eastern | 2 | HFO | 463
2023-05-24 02:00 | Eastern | 10 | Tripura | 96
2023-05-24 02:00 | Western | 1 | Gas | 969
2023-05-24 02:00 | Western | 6 | Coal | 1629
2023-05-24 02:00 | Western | 8 | HVDC | 838
2023-05-24 03:00 | Eastern | 1 | Gas | 4647
2023-05-24 03:00 | Eastern | 2 | HFO | 466
2023-05-24 03:00 | Eastern | 10 | Tripura | 108
2023-05-24 03:00 | Western | 1 | Gas | 880
2023-05-24 03:00 | Western | 6 | Coal | 1625
2023-05-24 03:00 | Western | 8 | HVDC | 907
2023-05-24 04:00 | Eastern | 1 | Gas | 4398
2023-05-24 04:00 | Eastern | 2 | HFO | 385
2023-05-24 04:00 | Eastern | 10 | Tripura | 108
2023-05-24 04:00 | Western | 1 | Gas | 822
2023-05-24 04:00 | Western | 6 | Coal | 1632
2023-05-24 04:00 | Western | 8 | HVDC | 909
2023-05-24 05:00 | Eastern | 1 | Gas | 4392
2023-05-24 05:00 | Eastern | 2 | HFO | 322
2023-05-24 05:00 | Eastern | 10 | Tripura | 104
2023-05-24 05:00 | Western | 1 | Gas | 823
2023-05-24 05:00 | Western | 6 | Coal | 1623
2023-05-24 05:00 | Western | 8 | HVDC | 907
2023-05-24 06:00 | Eastern | 1 | Gas | 4177.79
2023-05-24 06:00 | Eastern | 2 | HFO | 318
2023-05-24 06:00 | Eastern | 10 | Tripura | 94
2023-05-24 06:00 | Eastern | 11 | Solar | 3
2023-05-24 06:00 | Western | 1 | Gas | 966
2023-05-24 06:00 | Western | 6 | Coal | 1620
2023-05-24 06:00 | Western | 8 | HVDC | 908
2023-05-24 06:00 | Western | 11 | Solar | 15.18
2023-05-24 07:00 | Eastern | 1 | Gas | 4188.79
2023-05-24 07:00 | Eastern | 2 | HFO | 578
2023-05-24 07:00 | Eastern | 10 | Tripura | 94
2023-05-24 07:00 | Eastern | 11 | Solar | 9
2023-05-24 07:00 | Western | 1 | Gas | 1046
2023-05-24 07:00 | Western | 6 | Coal | 1643
2023-05-24 07:00 | Western | 8 | HVDC | 909
2023-05-24 07:00 | Western | 11 | Solar | 75.09
2023-05-24 08:00 | Eastern | 1 | Gas | 4210.79
2023-05-24 08:00 | Eastern | 2 | HFO | 721
2023-05-24 08:00 | Eastern | 10 | Tripura | 104
2023-05-24 08:00 | Eastern | 11 | Solar | 34
2023-05-24 08:00 | Western | 1 | Gas | 1088
2023-05-24 08:00 | Western | 3 | HSD | 17
2023-05-24 08:00 | Western | 6 | Coal | 1660
2023-05-24 08:00 | Western | 8 | HVDC | 899
2023-05-24 08:00 | Western | 11 | Solar | 151.3
2023-05-24 09:00 | Eastern | 1 | Gas | 4349.79
2023-05-24 09:00 | Eastern | 2 | HFO | 870
2023-05-24 09:00 | Eastern | 5 | Hydro | 0
2023-05-24 09:00 | Eastern | 10 | Tripura | 116
2023-05-24 09:00 | Eastern | 11 | Solar | 71
2023-05-24 09:00 | Western | 1 | Gas | 1142
2023-05-24 09:00 | Western | 3 | HSD | 77
2023-05-24 09:00 | Western | 6 | Coal | 1649
2023-05-24 09:00 | Western | 8 | HVDC | 899
2023-05-24 09:00 | Western | 11 | Solar | 194.35
2023-05-24 10:00 | Eastern | 1 | Gas | 4058.79
2023-05-24 10:00 | Eastern | 2 | HFO | 1014
2023-05-24 10:00 | Eastern | 5 | Hydro | 25
2023-05-24 10:00 | Eastern | 10 | Tripura | 120
2023-05-24 10:00 | Eastern | 11 | Solar | 54
2023-05-24 10:00 | Western | 1 | Gas | 1072
2023-05-24 10:00 | Western | 3 | HSD | 85
2023-05-24 10:00 | Western | 6 | Coal | 1622
2023-05-24 10:00 | Western | 8 | HVDC | 854
2023-05-24 10:00 | Western | 11 | Solar | 286.87
2023-05-24 11:00 | Eastern | 1 | Gas | 4284.79
2023-05-24 11:00 | Eastern | 2 | HFO | 1158
2023-05-24 11:00 | Eastern | 5 | Hydro | 25
2023-05-24 11:00 | Eastern | 10 | Tripura | 108
2023-05-24 11:00 | Eastern | 11 | Solar | 67
2023-05-24 11:00 | Western | 1 | Gas | 1151
2023-05-24 11:00 | Western | 3 | HSD | 216
2023-05-24 11:00 | Western | 6 | Coal | 1624
2023-05-24 11:00 | Western | 8 | HVDC | 894
2023-05-24 11:00 | Western | 11 | Solar | 344.23
2023-05-24 12:00 | Eastern | 1 | Gas | 4292.79
2023-05-24 12:00 | Eastern | 2 | HFO | 1314
2023-05-24 12:00 | Eastern | 3 | HSD | 118
2023-05-24 12:00 | Eastern | 5 | Hydro | 25
2023-05-24 12:00 | Eastern | 10 | Tripura | 112
2023-05-24 12:00 | Eastern | 11 | Solar | 83
2023-05-24 12:00 | Western | 1 | Gas | 824
2023-05-24 12:00 | Western | 3 | HSD | 308
2023-05-24 12:00 | Western | 6 | Coal | 1774
2023-05-24 12:00 | Western | 8 | HVDC | 893
2023-05-24 12:00 | Western | 11 | Solar | 291.37
2023-05-24 13:00 | Eastern | 1 | Gas | 4270.79
2023-05-24 13:00 | Eastern | 2 | HFO | 1369
2023-05-24 13:00 | Eastern | 3 | HSD | 164
2023-05-24 13:00 | Eastern | 5 | Hydro | 25
2023-05-24 13:00 | Eastern | 10 | Tripura | 122
2023-05-24 13:00 | Eastern | 11 | Solar | 78
2023-05-24 13:00 | Western | 1 | Gas | 811
2023-05-24 13:00 | Western | 2 | HFO | 61
2023-05-24 13:00 | Western | 3 | HSD | 364
2023-05-24 13:00 | Western | 6 | Coal | 2069
2023-05-24 13:00 | Western | 8 | HVDC | 894
2023-05-24 13:00 | Western | 11 | Solar | 315.33
2023-05-24 14:00 | Eastern | 1 | Gas | 4438.79
2023-05-24 14:00 | Eastern | 2 | HFO | 1370
2023-05-24 14:00 | Eastern | 3 | HSD | 50
2023-05-24 14:00 | Eastern | 5 | Hydro | 25
2023-05-24 14:00 | Eastern | 10 | Tripura | 142
2023-05-24 14:00 | Eastern | 11 | Solar | 86
2023-05-24 14:00 | Western | 1 | Gas | 848
2023-05-24 14:00 | Western | 2 | HFO | 157
2023-05-24 14:00 | Western | 3 | HSD | 368
2023-05-24 14:00 | Western | 6 | Coal | 2073
2023-05-24 14:00 | Western | 8 | HVDC | 894
2023-05-24 14:00 | Western | 11 | Solar | 281.86
2023-05-24 15:00 | Eastern | 1 | Gas | 4608.79
2023-05-24 15:00 | Eastern | 2 | HFO | 1338
2023-05-24 15:00 | Eastern | 3 | HSD | 50
2023-05-24 15:00 | Eastern | 5 | Hydro | 25
2023-05-24 15:00 | Eastern | 6 | Coal | 50
2023-05-24 15:00 | Eastern | 10 | Tripura | 134
2023-05-24 15:00 | Eastern | 11 | Solar | 69
2023-05-24 15:00 | Western | 1 | Gas | 937
2023-05-24 15:00 | Western | 2 | HFO | 168
2023-05-24 15:00 | Western | 3 | HSD | 363
2023-05-24 15:00 | Western | 6 | Coal | 2046
2023-05-24 15:00 | Western | 8 | HVDC | 894
2023-05-24 15:00 | Western | 11 | Solar | 207.81
2023-05-24 16:00 | Eastern | 1 | Gas | 4641.79
2023-05-24 16:00 | Eastern | 2 | HFO | 1324
2023-05-24 16:00 | Eastern | 3 | HSD | 230
2023-05-24 16:00 | Eastern | 5 | Hydro | 25
2023-05-24 16:00 | Eastern | 6 | Coal | 110
2023-05-24 16:00 | Eastern | 10 | Tripura | 134
2023-05-24 16:00 | Eastern | 11 | Solar | 38
2023-05-24 16:00 | Western | 1 | Gas | 1236
2023-05-24 16:00 | Western | 2 | HFO | 122
2023-05-24 16:00 | Western | 3 | HSD | 365
2023-05-24 16:00 | Western | 6 | Coal | 1841
2023-05-24 16:00 | Western | 8 | HVDC | 894
2023-05-24 16:00 | Western | 11 | Solar | 134.61
2023-05-24 17:00 | Eastern | 1 | Gas | 4736.79
2023-05-24 17:00 | Eastern | 2 | HFO | 1388
2023-05-24 17:00 | Eastern | 5 | Hydro | 25
2023-05-24 17:00 | Eastern | 6 | Coal | 141
2023-05-24 17:00 | Eastern | 10 | Tripura | 118
2023-05-24 17:00 | Eastern | 11 | Solar | 18
2023-05-24 17:00 | Western | 1 | Gas | 1132
2023-05-24 17:00 | Western | 2 | HFO | 52
2023-05-24 17:00 | Western | 3 | HSD | 363
2023-05-24 17:00 | Western | 6 | Coal | 1798
2023-05-24 17:00 | Western | 8 | HVDC | 905
2023-05-24 17:00 | Western | 11 | Solar | 64.16
2023-05-24 18:00 | Eastern | 1 | Gas | 4740.79
2023-05-24 18:00 | Eastern | 2 | HFO | 1383
2023-05-24 18:00 | Eastern | 5 | Hydro | 25
2023-05-24 18:00 | Eastern | 10 | Tripura | 124
2023-05-24 18:00 | Eastern | 11 | Solar | 5
2023-05-24 18:00 | Western | 1 | Gas | 1145
2023-05-24 18:00 | Western | 2 | HFO | 82
2023-05-24 18:00 | Western | 3 | HSD | 301
2023-05-24 18:00 | Western | 6 | Coal | 1808
2023-05-24 18:00 | Western | 8 | HVDC | 905
2023-05-24 18:00 | Western | 11 | Solar | 17.25
2023-05-24 19:00 | Eastern | 1 | Gas | 4794.79
2023-05-24 19:00 | Eastern | 2 | HFO | 2186
2023-05-24 19:00 | Eastern | 3 | HSD | 102
2023-05-24 19:00 | Eastern | 5 | Hydro | 25
2023-05-24 19:00 | Eastern | 10 | Tripura | 132
2023-05-24 19:00 | Western | 1 | Gas | 1220
2023-05-24 19:00 | Western | 2 | HFO | 379
2023-05-24 19:00 | Western | 3 | HSD | 359
2023-05-24 19:00 | Western | 6 | Coal | 1883
2023-05-24 19:00 | Western | 8 | HVDC | 904
2023-05-24 19:00 | Western | 11 | Solar | 0
2023-05-24 19:30 | Eastern | 1 | Gas | 4613.79
2023-05-24 19:30 | Eastern | 2 | HFO | 2601
2023-05-24 19:30 | Eastern | 5 | Hydro | 25
2023-05-24 19:30 | Eastern | 10 | Tripura | 142
2023-05-24 19:30 | Western | 1 | Gas | 1291
2023-05-24 19:30 | Western | 2 | HFO | 587
2023-05-24 19:30 | Western | 3 | HSD | 363
2023-05-24 19:30 | Western | 6 | Coal | 2119
2023-05-24 19:30 | Western | 8 | HVDC | 905
2023-05-24 20:00 | Eastern | 1 | Gas | 4666.79
2023-05-24 20:00 | Eastern | 2 | HFO | 2534
2023-05-24 20:00 | Eastern | 5 | Hydro | 25
2023-05-24 20:00 | Eastern | 10 | Tripura | 136
2023-05-24 20:00 | Western | 1 | Gas | 1279
2023-05-24 20:00 | Western | 2 | HFO | 483
2023-05-24 20:00 | Western | 3 | HSD | 249
2023-05-24 20:00 | Western | 6 | Coal | 2126
2023-05-24 20:00 | Western | 8 | HVDC | 905
2023-05-24 21:00 | Eastern | 1 | Gas | 4745.79
2023-05-24 21:00 | Eastern | 2 | HFO | 2375
2023-05-24 21:00 | Eastern | 5 | Hydro | 25
2023-05-24 21:00 | Eastern | 10 | Tripura | 138
2023-05-24 21:00 | Western | 1 | Gas | 1417
2023-05-24 21:00 | Western | 2 | HFO | 486
2023-05-24 21:00 | Western | 6 | Coal | 2255
2023-05-24 21:00 | Western | 8 | HVDC | 828
2023-05-24 22:00 | Eastern | 1 | Gas | 4829.79
2023-05-24 22:00 | Eastern | 2 | HFO | 2026
2023-05-24 22:00 | Eastern | 5 | Hydro | 25
2023-05-24 22:00 | Eastern | 10 | Tripura | 144
2023-05-24 22:00 | Western | 1 | Gas | 1375
2023-05-24 22:00 | Western | 2 | HFO | 272
2023-05-24 22:00 | Western | 6 | Coal | 2465
2023-05-24 22:00 | Western | 8 | HVDC | 828
2023-05-24 23:00 | Eastern | 1 | Gas | 5012.79
2023-05-24 23:00 | Eastern | 2 | HFO | 1499
2023-05-24 23:00 | Eastern | 5 | Hydro | 0
2023-05-24 23:00 | Eastern | 10 | Tripura | 136
2023-05-24 23:00 | Western | 1 | Gas | 1337
2023-05-24 23:00 | Western | 2 | HFO | 266
2023-05-24 23:00 | Western | 6 | Coal | 2494
2023-05-24 23:00 | Western | 8 | HVDC | 841
2023-05-25 | Eastern | 1 | Gas | 5261.79
2023-05-25 | Eastern | 2 | HFO | 1170
2023-05-25 | Eastern | 10 | Tripura | 136
2023-05-25 | Eastern | 11 | Solar | 0
2023-05-25 | Western | 1 | Gas | 1347
2023-05-25 | Western | 2 | HFO | 186
2023-05-25 | Western | 6 | Coal | 2377
2023-05-25 | Western | 8 | HVDC | 841
2023-05-25 | Western | 11 | Solar | 0
2023-05-25 01:00 | Eastern | 1 | Gas | 5212.79
2023-05-25 01:00 | Eastern | 2 | HFO | 804
2023-05-25 01:00 | Eastern | 10 | Tripura | 118
2023-05-25 01:00 | Western | 1 | Gas | 1341
2023-05-25 01:00 | Western | 2 | HFO | 122
2023-05-25 01:00 | Western | 6 | Coal | 2474
2023-05-25 01:00 | Western | 8 | HVDC | 816
2023-05-25 02:00 | Eastern | 1 | Gas | 5150.79
2023-05-25 02:00 | Eastern | 2 | HFO | 636
2023-05-25 02:00 | Eastern | 10 | Tripura | 122
2023-05-25 02:00 | Western | 1 | Gas | 1298
2023-05-25 02:00 | Western | 2 | HFO | 17
2023-05-25 02:00 | Western | 6 | Coal | 2371
2023-05-25 02:00 | Western | 8 | HVDC | 914
2023-05-25 03:00 | Eastern | 1 | Gas | 4997.79
2023-05-25 03:00 | Eastern | 2 | HFO | 545
2023-05-25 03:00 | Eastern | 10 | Tripura | 112
2023-05-25 03:00 | Western | 1 | Gas | 1180
2023-05-25 03:00 | Western | 6 | Coal | 2379
2023-05-25 03:00 | Western | 8 | HVDC | 914
2023-05-25 04:00 | Eastern | 1 | Gas | 4805.79
2023-05-25 04:00 | Eastern | 2 | HFO | 493
2023-05-25 04:00 | Eastern | 10 | Tripura | 108
2023-05-25 04:00 | Western | 1 | Gas | 1125
2023-05-25 04:00 | Western | 6 | Coal | 2345
2023-05-25 04:00 | Western | 8 | HVDC | 909
2023-05-25 05:00 | Eastern | 1 | Gas | 4477.79
2023-05-25 05:00 | Eastern | 2 | HFO | 463
2023-05-25 05:00 | Eastern | 10 | Tripura | 116
2023-05-25 05:00 | Western | 1 | Gas | 1124
2023-05-25 05:00 | Western | 6 | Coal | 2299
2023-05-25 05:00 | Western | 8 | HVDC | 913
2023-05-25 06:00 | Eastern | 1 | Gas | 4228
2023-05-25 06:00 | Eastern | 2 | HFO | 340
2023-05-25 06:00 | Eastern | 10 | Tripura | 104
2023-05-25 06:00 | Eastern | 11 | Solar | 6
2023-05-25 06:00 | Western | 1 | Gas | 1083
2023-05-25 06:00 | Western | 6 | Coal | 2232
2023-05-25 06:00 | Western | 8 | HVDC | 913
2023-05-25 06:00 | Western | 11 | Solar | 19.14
2023-05-25 07:00 | Eastern | 1 | Gas | 4284
2023-05-25 07:00 | Eastern | 2 | HFO | 339
2023-05-25 07:00 | Eastern | 10 | Tripura | 108
2023-05-25 07:00 | Eastern | 11 | Solar | 23
2023-05-25 07:00 | Western | 1 | Gas | 1131
2023-05-25 07:00 | Western | 3 | HSD | 0
2023-05-25 07:00 | Western | 6 | Coal | 2230
2023-05-25 07:00 | Western | 8 | HVDC | 913
2023-05-25 07:00 | Western | 11 | Solar | 68.08
2023-05-25 08:00 | Eastern | 1 | Gas | 4298
2023-05-25 08:00 | Eastern | 2 | HFO | 341
2023-05-25 08:00 | Eastern | 10 | Tripura | 120
2023-05-25 08:00 | Eastern | 11 | Solar | 47
2023-05-25 08:00 | Western | 1 | Gas | 1130
2023-05-25 08:00 | Western | 2 | HFO | 0
2023-05-25 08:00 | Western | 3 | HSD | 20
2023-05-25 08:00 | Western | 6 | Coal | 2208
2023-05-25 08:00 | Western | 8 | HVDC | 913
2023-05-25 08:00 | Western | 11 | Solar | 169.46
2023-05-25 09:00 | Eastern | 1 | Gas | 4964.79
2023-05-25 09:00 | Eastern | 2 | HFO | 462
2023-05-25 09:00 | Eastern | 5 | Hydro | 0
2023-05-25 09:00 | Eastern | 10 | Tripura | 122
2023-05-25 09:00 | Eastern | 11 | Solar | 67
2023-05-25 09:00 | Western | 1 | Gas | 1131
2023-05-25 09:00 | Western | 2 | HFO | 1
2023-05-25 09:00 | Western | 3 | HSD | 20
2023-05-25 09:00 | Western | 6 | Coal | 2135
2023-05-25 09:00 | Western | 8 | HVDC | 913
2023-05-25 09:00 | Western | 11 | Solar | 251.54
2023-05-25 10:00 | Eastern | 1 | Gas | 4821
2023-05-25 10:00 | Eastern | 2 | HFO | 934
2023-05-25 10:00 | Eastern | 5 | Hydro | 25
2023-05-25 10:00 | Eastern | 10 | Tripura | 132
2023-05-25 10:00 | Eastern | 11 | Solar | 79
2023-05-25 10:00 | Western | 1 | Gas | 1118
2023-05-25 10:00 | Western | 2 | HFO | 127
2023-05-25 10:00 | Western | 3 | HSD | 20
2023-05-25 10:00 | Western | 6 | Coal | 2234
2023-05-25 10:00 | Western | 8 | HVDC | 913
2023-05-25 10:00 | Western | 11 | Solar | 280.35
2023-05-25 11:00 | Eastern | 1 | Gas | 4971.79
2023-05-25 11:00 | Eastern | 2 | HFO | 1221
2023-05-25 11:00 | Eastern | 3 | HSD | 0
2023-05-25 11:00 | Eastern | 5 | Hydro | 25
2023-05-25 11:00 | Eastern | 10 | Tripura | 142
2023-05-25 11:00 | Eastern | 11 | Solar | 94
2023-05-25 11:00 | Western | 1 | Gas | 1114
2023-05-25 11:00 | Western | 2 | HFO | 153
2023-05-25 11:00 | Western | 3 | HSD | 130
2023-05-25 11:00 | Western | 6 | Coal | 2237
2023-05-25 11:00 | Western | 8 | HVDC | 913
2023-05-25 11:00 | Western | 11 | Solar | 267.21
2023-05-25 12:00 | Eastern | 1 | Gas | 4984.79
2023-05-25 12:00 | Eastern | 2 | HFO | 1279
2023-05-25 12:00 | Eastern | 3 | HSD | 194
2023-05-25 12:00 | Eastern | 5 | Hydro | 25
2023-05-25 12:00 | Eastern | 10 | Tripura | 152
2023-05-25 12:00 | Eastern | 11 | Solar | 112
2023-05-25 12:00 | Western | 1 | Gas | 1116
2023-05-25 12:00 | Western | 2 | HFO | 158
2023-05-25 12:00 | Western | 3 | HSD | 304
2023-05-25 12:00 | Western | 6 | Coal | 2234
2023-05-25 12:00 | Western | 8 | HVDC | 913
2023-05-25 12:00 | Western | 11 | Solar | 276.27
2023-05-25 13:00 | Eastern | 1 | Gas | 4947.79
2023-05-25 13:00 | Eastern | 2 | HFO | 1320
2023-05-25 13:00 | Eastern | 3 | HSD | 395
2023-05-25 13:00 | Eastern | 5 | Hydro | 25
2023-05-25 13:00 | Eastern | 6 | Coal | 0
2023-05-25 13:00 | Eastern | 10 | Tripura | 146
2023-05-25 13:00 | Eastern | 11 | Solar | 100
2023-05-25 13:00 | Western | 1 | Gas | 1115
2023-05-25 13:00 | Western | 2 | HFO | 177
2023-05-25 13:00 | Western | 3 | HSD | 305
2023-05-25 13:00 | Western | 6 | Coal | 2242
2023-05-25 13:00 | Western | 8 | HVDC | 914
2023-05-25 13:00 | Western | 11 | Solar | 240.29
2023-05-25 14:00 | Eastern | 1 | Gas | 4936.79
2023-05-25 14:00 | Eastern | 2 | HFO | 1360
2023-05-25 14:00 | Eastern | 3 | HSD | 370
2023-05-25 14:00 | Eastern | 5 | Hydro | 25
2023-05-25 14:00 | Eastern | 6 | Coal | 75
2023-05-25 14:00 | Eastern | 10 | Tripura | 140
2023-05-25 14:00 | Eastern | 11 | Solar | 93
2023-05-25 14:00 | Western | 1 | Gas | 1185
2023-05-25 14:00 | Western | 2 | HFO | 189
2023-05-25 14:00 | Western | 3 | HSD | 314
2023-05-25 14:00 | Western | 6 | Coal | 2228
2023-05-25 14:00 | Western | 8 | HVDC | 913
2023-05-25 14:00 | Western | 11 | Solar | 288.58
2023-05-25 15:00 | Eastern | 1 | Gas | 4921.79
2023-05-25 15:00 | Eastern | 2 | HFO | 1356
2023-05-25 15:00 | Eastern | 3 | HSD | 459
2023-05-25 15:00 | Eastern | 5 | Hydro | 25
2023-05-25 15:00 | Eastern | 6 | Coal | 125
2023-05-25 15:00 | Eastern | 10 | Tripura | 142
2023-05-25 15:00 | Eastern | 11 | Solar | 62
2023-05-25 15:00 | Western | 1 | Gas | 1250
2023-05-25 15:00 | Western | 2 | HFO | 160
2023-05-25 15:00 | Western | 3 | HSD | 202
2023-05-25 15:00 | Western | 6 | Coal | 2211
2023-05-25 15:00 | Western | 8 | HVDC | 914
2023-05-25 15:00 | Western | 11 | Solar | 240.11
2023-05-25 16:00 | Eastern | 1 | Gas | 5033.79
2023-05-25 16:00 | Eastern | 2 | HFO | 1421
2023-05-25 16:00 | Eastern | 5 | Hydro | 25
2023-05-25 16:00 | Eastern | 6 | Coal | 125
2023-05-25 16:00 | Eastern | 10 | Tripura | 136
2023-05-25 16:00 | Eastern | 11 | Solar | 47
2023-05-25 16:00 | Western | 1 | Gas | 1230
2023-05-25 16:00 | Western | 2 | HFO | 211
2023-05-25 16:00 | Western | 6 | Coal | 2284
2023-05-25 16:00 | Western | 8 | HVDC | 915
2023-05-25 16:00 | Western | 11 | Solar | 132.11
2023-05-25 17:00 | Eastern | 1 | Gas | 5011.79
2023-05-25 17:00 | Eastern | 2 | HFO | 1536
2023-05-25 17:00 | Eastern | 5 | Hydro | 25
2023-05-25 17:00 | Eastern | 6 | Coal | 130
2023-05-25 17:00 | Eastern | 10 | Tripura | 126
2023-05-25 17:00 | Eastern | 11 | Solar | 20
2023-05-25 17:00 | Western | 1 | Gas | 1213
2023-05-25 17:00 | Western | 2 | HFO | 257
2023-05-25 17:00 | Western | 6 | Coal | 2286
2023-05-25 17:00 | Western | 8 | HVDC | 914
2023-05-25 17:00 | Western | 11 | Solar | 58
2023-05-25 18:00 | Eastern | 1 | Gas | 4791
2023-05-25 18:00 | Eastern | 2 | HFO | 1636
2023-05-25 18:00 | Eastern | 5 | Hydro | 25
2023-05-25 18:00 | Eastern | 6 | Coal | 165
2023-05-25 18:00 | Eastern | 10 | Tripura | 138
2023-05-25 18:00 | Eastern | 11 | Solar | 4
2023-05-25 18:00 | Western | 1 | Gas | 1159
2023-05-25 18:00 | Western | 2 | HFO | 268
2023-05-25 18:00 | Western | 6 | Coal | 2088
2023-05-25 18:00 | Western | 8 | HVDC | 914
2023-05-25 18:00 | Western | 11 | Solar | 16.23
2023-05-25 19:00 | Eastern | 1 | Gas | 5066.79
2023-05-25 19:00 | Eastern | 2 | HFO | 2404
2023-05-25 19:00 | Eastern | 3 | HSD | 292
2023-05-25 19:00 | Eastern | 5 | Hydro | 25
2023-05-25 19:00 | Eastern | 6 | Coal | 245
2023-05-25 19:00 | Eastern | 10 | Tripura | 140
2023-05-25 19:00 | Western | 1 | Gas | 1195
2023-05-25 19:00 | Western | 2 | HFO | 603
2023-05-25 19:00 | Western | 6 | Coal | 2121
2023-05-25 19:00 | Western | 8 | HVDC | 912
2023-05-25 19:30 | Eastern | 1 | Gas | 5046.79
2023-05-25 19:30 | Eastern | 2 | HFO | 2655
2023-05-25 19:30 | Eastern | 3 | HSD | 257
2023-05-25 19:30 | Eastern | 5 | Hydro | 25
2023-05-25 19:30 | Eastern | 6 | Coal | 250
2023-05-25 19:30 | Eastern | 10 | Tripura | 136
2023-05-25 19:30 | Western | 1 | Gas | 1105
2023-05-25 19:30 | Western | 2 | HFO | 856
2023-05-25 19:30 | Western | 6 | Coal | 2247
2023-05-25 19:30 | Western | 8 | HVDC | 913
2023-05-25 20:00 | Eastern | 1 | Gas | 5096.79
2023-05-25 20:00 | Eastern | 2 | HFO | 2737
2023-05-25 20:00 | Eastern | 3 | HSD | 50
2023-05-25 20:00 | Eastern | 5 | Hydro | 25
2023-05-25 20:00 | Eastern | 6 | Coal | 255
2023-05-25 20:00 | Eastern | 10 | Tripura | 142
2023-05-25 20:00 | Western | 1 | Gas | 1097
2023-05-25 20:00 | Western | 2 | HFO | 936
2023-05-25 20:00 | Western | 6 | Coal | 2255
2023-05-25 20:00 | Western | 8 | HVDC | 914
2023-05-25 21:00 | Eastern | 1 | Gas | 5063.79
2023-05-25 21:00 | Eastern | 2 | HFO | 2535
2023-05-25 21:00 | Eastern | 5 | Hydro | 25
2023-05-25 21:00 | Eastern | 6 | Coal | 265
2023-05-25 21:00 | Eastern | 10 | Tripura | 140
2023-05-25 21:00 | Western | 1 | Gas | 1044
2023-05-25 21:00 | Western | 2 | HFO | 452
2023-05-25 21:00 | Western | 6 | Coal | 1496
2023-05-25 21:00 | Western | 8 | HVDC | 913
2023-05-25 22:00 | Eastern | 1 | Gas | 4963.79
2023-05-25 22:00 | Eastern | 2 | HFO | 1757
2023-05-25 22:00 | Eastern | 5 | Hydro | 25
2023-05-25 22:00 | Eastern | 6 | Coal | 275
2023-05-25 22:00 | Eastern | 10 | Tripura | 148
2023-05-25 22:00 | Western | 1 | Gas | 1046
2023-05-25 22:00 | Western | 2 | HFO | 16
2023-05-25 22:00 | Western | 6 | Coal | 1901
2023-05-25 22:00 | Western | 8 | HVDC | 914
2023-05-25 23:00 | Eastern | 1 | Gas | 4776.79
2023-05-25 23:00 | Eastern | 2 | HFO | 1052
2023-05-25 23:00 | Eastern | 5 | Hydro | 0
2023-05-25 23:00 | Eastern | 6 | Coal | 295
2023-05-25 23:00 | Eastern | 10 | Tripura | 148
2023-05-25 23:00 | Western | 1 | Gas | 845
2023-05-25 23:00 | Western | 6 | Coal | 1552
2023-05-25 23:00 | Western | 8 | HVDC | 914
2023-05-26 | Eastern | 1 | Gas | 4620
2023-05-26 | Eastern | 2 | HFO | 781
2023-05-26 | Eastern | 3 | HSD | 0
2023-05-26 | Eastern | 6 | Coal | 294
2023-05-26 | Eastern | 10 | Tripura | 152
2023-05-26 | Western | 1 | Gas | 819
2023-05-26 | Western | 2 | HFO | 0
2023-05-26 | Western | 6 | Coal | 1499
2023-05-26 | Western | 8 | HVDC | 914
2023-05-26 01:00 | Eastern | 1 | Gas | 4685
2023-05-26 01:00 | Eastern | 2 | HFO | 645
2023-05-26 01:00 | Eastern | 6 | Coal | 285
2023-05-26 01:00 | Eastern | 10 | Tripura | 146
2023-05-26 01:00 | Western | 1 | Gas | 883
2023-05-26 01:00 | Western | 6 | Coal | 1501
2023-05-26 01:00 | Western | 8 | HVDC | 914
2023-05-26 02:00 | Eastern | 1 | Gas | 4735
2023-05-26 02:00 | Eastern | 2 | HFO | 583
2023-05-26 02:00 | Eastern | 6 | Coal | 235
2023-05-26 02:00 | Eastern | 10 | Tripura | 146
2023-05-26 02:00 | Western | 1 | Gas | 938
2023-05-26 02:00 | Western | 6 | Coal | 1498
2023-05-26 02:00 | Western | 8 | HVDC | 914
2023-05-26 03:00 | Eastern | 1 | Gas | 4624
2023-05-26 03:00 | Eastern | 2 | HFO | 584
2023-05-26 03:00 | Eastern | 6 | Coal | 230
2023-05-26 03:00 | Eastern | 10 | Tripura | 144
2023-05-26 03:00 | Western | 1 | Gas | 976
2023-05-26 03:00 | Western | 6 | Coal | 1514
2023-05-26 03:00 | Western | 8 | HVDC | 903
2023-05-26 04:00 | Eastern | 1 | Gas | 4596
2023-05-26 04:00 | Eastern | 2 | HFO | 598
2023-05-26 04:00 | Eastern | 6 | Coal | 260
2023-05-26 04:00 | Eastern | 10 | Tripura | 136
2023-05-26 04:00 | Western | 1 | Gas | 1026
2023-05-26 04:00 | Western | 6 | Coal | 1452
2023-05-26 04:00 | Western | 8 | HVDC | 903
2023-05-26 05:00 | Eastern | 1 | Gas | 4367
2023-05-26 05:00 | Eastern | 2 | HFO | 491
2023-05-26 05:00 | Eastern | 6 | Coal | 295
2023-05-26 05:00 | Eastern | 10 | Tripura | 130
2023-05-26 05:00 | Western | 1 | Gas | 1030
2023-05-26 05:00 | Western | 6 | Coal | 1414
2023-05-26 05:00 | Western | 8 | HVDC | 904
2023-05-26 06:00 | Eastern | 1 | Gas | 4102
2023-05-26 06:00 | Eastern | 2 | HFO | 340
2023-05-26 06:00 | Eastern | 6 | Coal | 275
2023-05-26 06:00 | Eastern | 10 | Tripura | 78
2023-05-26 06:00 | Eastern | 11 | Solar | 6
2023-05-26 06:00 | Western | 1 | Gas | 981
2023-05-26 06:00 | Western | 6 | Coal | 1365
2023-05-26 06:00 | Western | 8 | HVDC | 902
2023-05-26 06:00 | Western | 11 | Solar | 20.27
2023-05-26 07:00 | Eastern | 1 | Gas | 4169
2023-05-26 07:00 | Eastern | 2 | HFO | 241
2023-05-26 07:00 | Eastern | 6 | Coal | 280
2023-05-26 07:00 | Eastern | 10 | Tripura | 80
2023-05-26 07:00 | Eastern | 11 | Solar | 27
2023-05-26 07:00 | Western | 1 | Gas | 934
2023-05-26 07:00 | Western | 6 | Coal | 1368
2023-05-26 07:00 | Western | 8 | HVDC | 903
2023-05-26 07:00 | Western | 11 | Solar | 33.92
2023-05-26 08:00 | Eastern | 1 | Gas | 4104
2023-05-26 08:00 | Eastern | 2 | HFO | 184
2023-05-26 08:00 | Eastern | 6 | Coal | 302
2023-05-26 08:00 | Eastern | 10 | Tripura | 84
2023-05-26 08:00 | Eastern | 11 | Solar | 54
2023-05-26 08:00 | Western | 1 | Gas | 971
2023-05-26 08:00 | Western | 6 | Coal | 1371
2023-05-26 08:00 | Western | 8 | HVDC | 903
2023-05-26 08:00 | Western | 11 | Solar | 182.56
2023-05-26 09:00 | Eastern | 1 | Gas | 4498
2023-05-26 09:00 | Eastern | 2 | HFO | 199
2023-05-26 09:00 | Eastern | 5 | Hydro | 0
2023-05-26 09:00 | Eastern | 6 | Coal | 311
2023-05-26 09:00 | Eastern | 10 | Tripura | 92
2023-05-26 09:00 | Eastern | 11 | Solar | 84
2023-05-26 09:00 | Western | 1 | Gas | 978
2023-05-26 09:00 | Western | 6 | Coal | 1363
2023-05-26 09:00 | Western | 8 | HVDC | 902
2023-05-26 09:00 | Western | 11 | Solar | 155.93
2023-05-26 10:00 | Eastern | 1 | Gas | 4746.79
2023-05-26 10:00 | Eastern | 2 | HFO | 200
2023-05-26 10:00 | Eastern | 5 | Hydro | 25
2023-05-26 10:00 | Eastern | 6 | Coal | 340
2023-05-26 10:00 | Eastern | 10 | Tripura | 88
2023-05-26 10:00 | Eastern | 11 | Solar | 100
2023-05-26 10:00 | Western | 1 | Gas | 951
2023-05-26 10:00 | Western | 6 | Coal | 1362
2023-05-26 10:00 | Western | 8 | HVDC | 903
2023-05-26 10:00 | Western | 11 | Solar | 300.8
2023-05-26 11:00 | Eastern | 1 | Gas | 5007.79
2023-05-26 11:00 | Eastern | 2 | HFO | 379
2023-05-26 11:00 | Eastern | 5 | Hydro | 25
2023-05-26 11:00 | Eastern | 6 | Coal | 364
2023-05-26 11:00 | Eastern | 10 | Tripura | 92
2023-05-26 11:00 | Eastern | 11 | Solar | 111
2023-05-26 11:00 | Western | 1 | Gas | 1025
2023-05-26 11:00 | Western | 6 | Coal | 1365
2023-05-26 11:00 | Western | 8 | HVDC | 903
2023-05-26 11:00 | Western | 11 | Solar | 315.08
2023-05-26 12:00 | Eastern | 1 | Gas | 5080.79
2023-05-26 12:00 | Eastern | 2 | HFO | 762.2
2023-05-26 12:00 | Eastern | 5 | Hydro | 25
2023-05-26 12:00 | Eastern | 6 | Coal | 387
2023-05-26 12:00 | Eastern | 10 | Tripura | 98
2023-05-26 12:00 | Eastern | 11 | Solar | 110
2023-05-26 12:00 | Western | 1 | Gas | 1138
2023-05-26 12:00 | Western | 2 | HFO | 1.5
2023-05-26 12:00 | Western | 6 | Coal | 1455
2023-05-26 12:00 | Western | 8 | HVDC | 903
2023-05-26 12:00 | Western | 11 | Solar | 325.3
2023-05-26 13:00 | Eastern | 1 | Gas | 4964.79
2023-05-26 13:00 | Eastern | 2 | HFO | 1081
2023-05-26 13:00 | Eastern | 5 | Hydro | 25
2023-05-26 13:00 | Eastern | 6 | Coal | 375
2023-05-26 13:00 | Eastern | 10 | Tripura | 98
2023-05-26 13:00 | Eastern | 11 | Solar | 104
2023-05-26 13:00 | Western | 1 | Gas | 1202
2023-05-26 13:00 | Western | 2 | HFO | 271
2023-05-26 13:00 | Western | 6 | Coal | 1651
2023-05-26 13:00 | Western | 8 | HVDC | 903
2023-05-26 13:00 | Western | 11 | Solar | 278
2023-05-26 14:00 | Eastern | 1 | Gas | 4758
2023-05-26 14:00 | Eastern | 2 | HFO | 1234
2023-05-26 14:00 | Eastern | 5 | Hydro | 25
2023-05-26 14:00 | Eastern | 6 | Coal | 393
2023-05-26 14:00 | Eastern | 10 | Tripura | 100
2023-05-26 14:00 | Eastern | 11 | Solar | 98
2023-05-26 14:00 | Western | 1 | Gas | 1056
2023-05-26 14:00 | Western | 2 | HFO | 331
2023-05-26 14:00 | Western | 6 | Coal | 1545
2023-05-26 14:00 | Western | 8 | HVDC | 903
2023-05-26 14:00 | Western | 11 | Solar | 234.58
2023-05-26 15:00 | Eastern | 1 | Gas | 5017.79
2023-05-26 15:00 | Eastern | 2 | HFO | 1220
2023-05-26 15:00 | Eastern | 5 | Hydro | 25
2023-05-26 15:00 | Eastern | 6 | Coal | 480
2023-05-26 15:00 | Eastern | 10 | Tripura | 110
2023-05-26 15:00 | Eastern | 11 | Solar | 78
2023-05-26 15:00 | Western | 1 | Gas | 1141.5
2023-05-26 15:00 | Western | 2 | HFO | 355
2023-05-26 15:00 | Western | 6 | Coal | 1634
2023-05-26 15:00 | Western | 8 | HVDC | 906
2023-05-26 15:00 | Western | 11 | Solar | 243.58
2023-05-26 16:00 | Eastern | 1 | Gas | 4899
2023-05-26 16:00 | Eastern | 2 | HFO | 1355
2023-05-26 16:00 | Eastern | 5 | Hydro | 25
2023-05-26 16:00 | Eastern | 6 | Coal | 445
2023-05-26 16:00 | Eastern | 10 | Tripura | 104
2023-05-26 16:00 | Eastern | 11 | Solar | 54
2023-05-26 16:00 | Western | 1 | Gas | 1065
2023-05-26 16:00 | Western | 2 | HFO | 301.9
2023-05-26 16:00 | Western | 6 | Coal | 1678
2023-05-26 16:00 | Western | 8 | HVDC | 908
2023-05-26 16:00 | Western | 11 | Solar | 145.45
2023-05-26 17:00 | Eastern | 1 | Gas | 4825
2023-05-26 17:00 | Eastern | 2 | HFO | 1326
2023-05-26 17:00 | Eastern | 5 | Hydro | 25
2023-05-26 17:00 | Eastern | 6 | Coal | 370
2023-05-26 17:00 | Eastern | 10 | Tripura | 104
2023-05-26 17:00 | Eastern | 11 | Solar | 20
2023-05-26 17:00 | Western | 1 | Gas | 1022
2023-05-26 17:00 | Western | 2 | HFO | 122.9
2023-05-26 17:00 | Western | 6 | Coal | 1721
2023-05-26 17:00 | Western | 8 | HVDC | 908
2023-05-26 17:00 | Western | 11 | Solar | 86
2023-05-26 18:00 | Eastern | 1 | Gas | 4612
2023-05-26 18:00 | Eastern | 2 | HFO | 1453
2023-05-26 18:00 | Eastern | 3 | HSD | 0
2023-05-26 18:00 | Eastern | 5 | Hydro | 25
2023-05-26 18:00 | Eastern | 6 | Coal | 335
2023-05-26 18:00 | Eastern | 10 | Tripura | 110
2023-05-26 18:00 | Eastern | 11 | Solar | 3
2023-05-26 18:00 | Western | 1 | Gas | 953
2023-05-26 18:00 | Western | 2 | HFO | 122.9
2023-05-26 18:00 | Western | 6 | Coal | 1722
2023-05-26 18:00 | Western | 8 | HVDC | 909
2023-05-26 18:00 | Western | 11 | Solar | 14.16
2023-05-26 19:00 | Eastern | 1 | Gas | 5026.79
2023-05-26 19:00 | Eastern | 2 | HFO | 2278
2023-05-26 19:00 | Eastern | 3 | HSD | 220
2023-05-26 19:00 | Eastern | 5 | Hydro | 25
2023-05-26 19:00 | Eastern | 6 | Coal | 270
2023-05-26 19:00 | Eastern | 10 | Tripura | 132
2023-05-26 19:00 | Eastern | 11 | Solar | 0
2023-05-26 19:00 | Western | 1 | Gas | 1042
2023-05-26 19:00 | Western | 2 | HFO | 510
2023-05-26 19:00 | Western | 6 | Coal | 1845
2023-05-26 19:00 | Western | 8 | HVDC | 909
2023-05-26 19:00 | Western | 11 | Solar | 0
2023-05-26 19:30 | Eastern | 1 | Gas | 4800
2023-05-26 19:30 | Eastern | 2 | HFO | 2546
2023-05-26 19:30 | Eastern | 3 | HSD | 0
2023-05-26 19:30 | Eastern | 5 | Hydro | 25
2023-05-26 19:30 | Eastern | 6 | Coal | 280
2023-05-26 19:30 | Eastern | 10 | Tripura | 130
2023-05-26 19:30 | Western | 1 | Gas | 1053
2023-05-26 19:30 | Western | 2 | HFO | 872
2023-05-26 19:30 | Western | 6 | Coal | 1933
2023-05-26 19:30 | Western | 8 | HVDC | 909
2023-05-26 20:00 | Eastern | 1 | Gas | 4485
2023-05-26 20:00 | Eastern | 2 | HFO | 2726
2023-05-26 20:00 | Eastern | 5 | Hydro | 25
2023-05-26 20:00 | Eastern | 6 | Coal | 275
2023-05-26 20:00 | Eastern | 10 | Tripura | 126
2023-05-26 20:00 | Western | 1 | Gas | 963
2023-05-26 20:00 | Western | 2 | HFO | 865
2023-05-26 20:00 | Western | 6 | Coal | 1936
2023-05-26 20:00 | Western | 8 | HVDC | 907
2023-05-26 20:00 | Western | 11 | Solar
2023-05-26 21:00 | Eastern | 1 | Gas | 4930
2023-05-26 21:00 | Eastern | 2 | HFO | 2312
2023-05-26 21:00 | Eastern | 5 | Hydro | 25
2023-05-26 21:00 | Eastern | 6 | Coal | 305
2023-05-26 21:00 | Eastern | 10 | Tripura | 132
2023-05-26 21:00 | Western | 1 | Gas | 956
2023-05-26 21:00 | Western | 2 | HFO | 414
2023-05-26 21:00 | Western | 3 | HSD | 0
2023-05-26 21:00 | Western | 6 | Coal | 1935
2023-05-26 21:00 | Western | 8 | HVDC | 903
2023-05-26 22:00 | Eastern | 1 | Gas | 5073
2023-05-26 22:00 | Eastern | 2 | HFO | 1764
2023-05-26 22:00 | Eastern | 5 | Hydro | 25
2023-05-26 22:00 | Eastern | 6 | Coal | 200
2023-05-26 22:00 | Eastern | 10 | Tripura | 148
2023-05-26 22:00 | Western | 1 | Gas | 1007
2023-05-26 22:00 | Western | 2 | HFO | 252
2023-05-26 22:00 | Western | 3 | HSD | 0
2023-05-26 22:00 | Western | 6 | Coal | 1940
2023-05-26 22:00 | Western | 8 | HVDC | 904
2023-05-26 23:00 | Eastern | 1 | Gas | 5330.79
2023-05-26 23:00 | Eastern | 2 | HFO | 1510
2023-05-26 23:00 | Eastern | 10 | Tripura | 102
2023-05-26 23:00 | Western | 1 | Gas | 1073
2023-05-26 23:00 | Western | 2 | HFO | 385
2023-05-26 23:00 | Western | 3 | HSD | 0
2023-05-26 23:00 | Western | 6 | Coal | 1938
2023-05-26 23:00 | Western | 8 | HVDC | 904
2023-05-27 | Eastern | 1 | Gas | 5290.79
2023-05-27 | Eastern | 2 | HFO | 1272
2023-05-27 | Eastern | 3 | HSD | 246
2023-05-27 | Eastern | 6 | Coal | 0
2023-05-27 | Eastern | 10 | Tripura | 132
2023-05-27 | Eastern | 11 | Solar | 0
2023-05-27 | Western | 1 | Gas | 1063
2023-05-27 | Western | 2 | HFO | 612
2023-05-27 | Western | 3 | HSD | 0
2023-05-27 | Western | 6 | Coal | 1985
2023-05-27 | Western | 8 | HVDC | 903
2023-05-27 | Western | 11 | Solar | 0
2023-05-27 01:00 | Eastern | 1 | Gas | 5275.79
2023-05-27 01:00 | Eastern | 2 | HFO | 1147
2023-05-27 01:00 | Eastern | 3 | HSD | 241
2023-05-27 01:00 | Eastern | 10 | Tripura | 150
2023-05-27 01:00 | Western | 1 | Gas | 1046
2023-05-27 01:00 | Western | 2 | HFO | 543
2023-05-27 01:00 | Western | 3 | HSD | 0
2023-05-27 01:00 | Western | 6 | Coal | 1992
2023-05-27 01:00 | Western | 8 | HVDC | 904
2023-05-27 02:00 | Eastern | 1 | Gas | 5291.79
2023-05-27 02:00 | Eastern | 2 | HFO | 1047
2023-05-27 02:00 | Eastern | 10 | Tripura | 148
2023-05-27 02:00 | Western | 1 | Gas | 1042
2023-05-27 02:00 | Western | 2 | HFO | 553
2023-05-27 02:00 | Western | 3 | HSD | 0
2023-05-27 02:00 | Western | 6 | Coal | 1993
2023-05-27 02:00 | Western | 8 | HVDC | 904
2023-05-27 03:00 | Eastern | 1 | Gas | 5291.79
2023-05-27 03:00 | Eastern | 2 | HFO | 1005
2023-05-27 03:00 | Eastern | 10 | Tripura | 148
2023-05-27 03:00 | Western | 1 | Gas | 1039
2023-05-27 03:00 | Western | 2 | HFO | 354
2023-05-27 03:00 | Western | 3 | HSD | 0
2023-05-27 03:00 | Western | 6 | Coal | 1887
2023-05-27 03:00 | Western | 8 | HVDC | 904
2023-05-27 04:00 | Eastern | 1 | Gas | 5293.79
2023-05-27 04:00 | Eastern | 2 | HFO | 860
2023-05-27 04:00 | Eastern | 10 | Tripura | 142
2023-05-27 04:00 | Western | 1 | Gas | 958
2023-05-27 04:00 | Western | 2 | HFO | 291
2023-05-27 04:00 | Western | 3 | HSD | 0
2023-05-27 04:00 | Western | 6 | Coal | 1839
2023-05-27 04:00 | Western | 8 | HVDC | 903
2023-05-27 05:00 | Eastern | 1 | Gas | 5081.79
2023-05-27 05:00 | Eastern | 2 | HFO | 843
2023-05-27 05:00 | Eastern | 10 | Tripura | 138
2023-05-27 05:00 | Western | 1 | Gas | 934
2023-05-27 05:00 | Western | 2 | HFO | 171
2023-05-27 05:00 | Western | 3 | HSD | 0
2023-05-27 05:00 | Western | 6 | Coal | 1810
2023-05-27 05:00 | Western | 8 | HVDC | 904
2023-05-27 06:00 | Eastern | 1 | Gas | 4905
2023-05-27 06:00 | Eastern | 2 | HFO | 836
2023-05-27 06:00 | Eastern | 10 | Tripura | 122
2023-05-27 06:00 | Eastern | 11 | Solar | 10
2023-05-27 06:00 | Western | 1 | Gas | 920
2023-05-27 06:00 | Western | 2 | HFO | 77
2023-05-27 06:00 | Western | 3 | HSD | 0
2023-05-27 06:00 | Western | 6 | Coal | 1759
2023-05-27 06:00 | Western | 8 | HVDC | 904
2023-05-27 06:00 | Western | 11 | Solar | 8.31
2023-05-27 07:00 | Eastern | 1 | Gas | 4893
2023-05-27 07:00 | Eastern | 2 | HFO | 818
2023-05-27 07:00 | Eastern | 10 | Tripura | 122
2023-05-27 07:00 | Eastern | 11 | Solar | 22
2023-05-27 07:00 | Western | 1 | Gas | 897
2023-05-27 07:00 | Western | 2 | HFO | 77
2023-05-27 07:00 | Western | 3 | HSD | 0
2023-05-27 07:00 | Western | 6 | Coal | 1761
2023-05-27 07:00 | Western | 8 | HVDC | 904
2023-05-27 07:00 | Western | 11 | Solar | 71.79
2023-05-27 08:00 | Eastern | 1 | Gas | 4985
2023-05-27 08:00 | Eastern | 2 | HFO | 810
2023-05-27 08:00 | Eastern | 10 | Tripura | 134
2023-05-27 08:00 | Eastern | 11 | Solar | 48
2023-05-27 08:00 | Western | 1 | Gas | 913
2023-05-27 08:00 | Western | 2 | HFO | 110
2023-05-27 08:00 | Western | 3 | HSD | 0
2023-05-27 08:00 | Western | 6 | Coal | 1771
2023-05-27 08:00 | Western | 8 | HVDC | 904
2023-05-27 08:00 | Western | 11 | Solar | 111.76
2023-05-27 09:00 | Eastern | 1 | Gas | 5174.79
2023-05-27 09:00 | Eastern | 2 | HFO | 827
2023-05-27 09:00 | Eastern | 10 | Tripura | 138
2023-05-27 09:00 | Eastern | 11 | Solar | 53
2023-05-27 09:00 | Western | 1 | Gas | 904
2023-05-27 09:00 | Western | 2 | HFO | 118
2023-05-27 09:00 | Western | 3 | HSD | 0
2023-05-27 09:00 | Western | 6 | Coal | 1819
2023-05-27 09:00 | Western | 8 | HVDC | 903
2023-05-27 09:00 | Western | 11 | Solar | 205.23
2023-05-27 10:00 | Eastern | 1 | Gas | 5187.79
2023-05-27 10:00 | Eastern | 2 | HFO | 878
2023-05-27 10:00 | Eastern | 5 | Hydro | 25
2023-05-27 10:00 | Eastern | 10 | Tripura | 154
2023-05-27 10:00 | Eastern | 11 | Solar | 62
2023-05-27 10:00 | Western | 1 | Gas | 960
2023-05-27 10:00 | Western | 2 | HFO | 161
2023-05-27 10:00 | Western | 3 | HSD | 0
2023-05-27 10:00 | Western | 6 | Coal | 1797
2023-05-27 10:00 | Western | 8 | HVDC | 904
2023-05-27 10:00 | Western | 11 | Solar | 206.29
2023-05-27 11:00 | Eastern | 1 | Gas | 5180.79
2023-05-27 11:00 | Eastern | 2 | HFO | 1036.48
2023-05-27 11:00 | Eastern | 5 | Hydro | 25
2023-05-27 11:00 | Eastern | 10 | Tripura | 158
2023-05-27 11:00 | Eastern | 11 | Solar | 48
2023-05-27 11:00 | Western | 1 | Gas | 995
2023-05-27 11:00 | Western | 2 | HFO | 241
2023-05-27 11:00 | Western | 3 | HSD | 0
2023-05-27 11:00 | Western | 6 | Coal | 1838
2023-05-27 11:00 | Western | 8 | HVDC | 904
2023-05-27 11:00 | Western | 11 | Solar | 131.43
2023-05-27 12:00 | Eastern | 1 | Gas | 5185.79
2023-05-27 12:00 | Eastern | 2 | HFO | 1166
2023-05-27 12:00 | Eastern | 5 | Hydro | 25
2023-05-27 12:00 | Eastern | 10 | Tripura | 164
2023-05-27 12:00 | Eastern | 11 | Solar | 27
2023-05-27 12:00 | Western | 1 | Gas | 998
2023-05-27 12:00 | Western | 2 | HFO | 337
2023-05-27 12:00 | Western | 3 | HSD | 0
2023-05-27 12:00 | Western | 6 | Coal | 1858
2023-05-27 12:00 | Western | 8 | HVDC | 905
2023-05-27 12:00 | Western | 11 | Solar | 115.83
2023-05-27 13:00 | Eastern | 1 | Gas | 4988
2023-05-27 13:00 | Eastern | 2 | HFO | 1206
2023-05-27 13:00 | Eastern | 5 | Hydro | 25
2023-05-27 13:00 | Eastern | 10 | Tripura | 170
2023-05-27 13:00 | Eastern | 11 | Solar | 36
2023-05-27 13:00 | Western | 1 | Gas | 976
2023-05-27 13:00 | Western | 2 | HFO | 358
2023-05-27 13:00 | Western | 3 | HSD | 0
2023-05-27 13:00 | Western | 6 | Coal | 1830
2023-05-27 13:00 | Western | 8 | HVDC | 903
2023-05-27 13:00 | Western | 11 | Solar | 84.73
2023-05-27 14:00 | Eastern | 1 | Gas | 4757
2023-05-27 14:00 | Eastern | 2 | HFO | 1216
2023-05-27 14:00 | Eastern | 5 | Hydro | 25
2023-05-27 14:00 | Eastern | 10 | Tripura | 168
2023-05-27 14:00 | Eastern | 11 | Solar | 44
2023-05-27 14:00 | Western | 1 | Gas | 913
2023-05-27 14:00 | Western | 2 | HFO | 293
2023-05-27 14:00 | Western | 3 | HSD | 0
2023-05-27 14:00 | Western | 6 | Coal | 1856
2023-05-27 14:00 | Western | 8 | HVDC | 903
2023-05-27 14:00 | Western | 11 | Solar | 154.87
2023-05-27 15:00 | Eastern | 1 | Gas | 4995.79
2023-05-27 15:00 | Eastern | 2 | HFO | 1145
2023-05-27 15:00 | Eastern | 5 | Hydro | 25
2023-05-27 15:00 | Eastern | 10 | Tripura | 90
2023-05-27 15:00 | Eastern | 11 | Solar | 46
2023-05-27 15:00 | Western | 1 | Gas | 980
2023-05-27 15:00 | Western | 2 | HFO | 293
2023-05-27 15:00 | Western | 3 | HSD | 0
2023-05-27 15:00 | Western | 6 | Coal | 1828
2023-05-27 15:00 | Western | 8 | HVDC | 903
2023-05-27 15:00 | Western | 11 | Solar | 182.74
2023-05-27 16:00 | Eastern | 1 | Gas | 4963.79
2023-05-27 16:00 | Eastern | 2 | HFO | 1029
2023-05-27 16:00 | Eastern | 5 | Hydro | 25
2023-05-27 16:00 | Eastern | 10 | Tripura | 114
2023-05-27 16:00 | Eastern | 11 | Solar | 31
2023-05-27 16:00 | Western | 1 | Gas | 947
2023-05-27 16:00 | Western | 2 | HFO | 257
2023-05-27 16:00 | Western | 3 | HSD | 0
2023-05-27 16:00 | Western | 6 | Coal | 1798
2023-05-27 16:00 | Western | 8 | HVDC | 904
2023-05-27 16:00 | Western | 11 | Solar | 147
2023-05-27 17:00 | Eastern | 1 | Gas | 4955.79
2023-05-27 17:00 | Eastern | 2 | HFO | 1121
2023-05-27 17:00 | Eastern | 5 | Hydro | 25
2023-05-27 17:00 | Eastern | 10 | Tripura | 120
2023-05-27 17:00 | Eastern | 11 | Solar | 19
2023-05-27 17:00 | Western | 1 | Gas | 923
2023-05-27 17:00 | Western | 2 | HFO | 289
2023-05-27 17:00 | Western | 3 | HSD | 0
2023-05-27 17:00 | Western | 6 | Coal | 1797
2023-05-27 17:00 | Western | 8 | HVDC | 903
2023-05-27 17:00 | Western | 11 | Solar | 82.31
2023-05-27 18:00 | Eastern | 1 | Gas | 4816
2023-05-27 18:00 | Eastern | 2 | HFO | 1254
2023-05-27 18:00 | Eastern | 5 | Hydro | 25
2023-05-27 18:00 | Eastern | 10 | Tripura | 120
2023-05-27 18:00 | Eastern | 11 | Solar | 7
2023-05-27 18:00 | Western | 1 | Gas | 927
2023-05-27 18:00 | Western | 2 | HFO | 305
2023-05-27 18:00 | Western | 3 | HSD | 0
2023-05-27 18:00 | Western | 6 | Coal | 1757
2023-05-27 18:00 | Western | 8 | HVDC | 904
2023-05-27 18:00 | Western | 11 | Solar | 21.25
2023-05-27 19:00 | Eastern | 1 | Gas | 5571.79
2023-05-27 19:00 | Eastern | 2 | HFO | 2009
2023-05-27 19:00 | Eastern | 5 | Hydro | 25
2023-05-27 19:00 | Eastern | 10 | Tripura | 144
2023-05-27 19:00 | Eastern | 11 | Solar | 0
2023-05-27 19:00 | Western | 1 | Gas | 937
2023-05-27 19:00 | Western | 2 | HFO | 533
2023-05-27 19:00 | Western | 3 | HSD | 0
2023-05-27 19:00 | Western | 6 | Coal | 1782
2023-05-27 19:00 | Western | 8 | HVDC | 904
2023-05-27 19:00 | Western | 11 | Solar | 0
2023-05-27 19:30 | Eastern | 1 | Gas | 5595.79
2023-05-27 19:30 | Eastern | 2 | HFO | 2449
2023-05-27 19:30 | Eastern | 5 | Hydro | 25
2023-05-27 19:30 | Eastern | 10 | Tripura | 148
2023-05-27 19:30 | Western | 1 | Gas | 932
2023-05-27 19:30 | Western | 2 | HFO | 754
2023-05-27 19:30 | Western | 3 | HSD | 0
2023-05-27 19:30 | Western | 6 | Coal | 1988
2023-05-27 19:30 | Western | 8 | HVDC | 904
2023-05-27 20:00 | Eastern | 1 | Gas | 5405.79
2023-05-27 20:00 | Eastern | 2 | HFO | 2513
2023-05-27 20:00 | Eastern | 5 | Hydro | 25
2023-05-27 20:00 | Eastern | 10 | Tripura | 144
2023-05-27 20:00 | Western | 1 | Gas | 935
2023-05-27 20:00 | Western | 2 | HFO | 830
2023-05-27 20:00 | Western | 3 | HSD | 0
2023-05-27 20:00 | Western | 6 | Coal | 2065
2023-05-27 20:00 | Western | 8 | HVDC | 904
2023-05-27 21:00 | Eastern | 1 | Gas | 5460.79
2023-05-27 21:00 | Eastern | 2 | HFO | 2547
2023-05-27 21:00 | Eastern | 5 | Hydro | 25
2023-05-27 21:00 | Eastern | 10 | Tripura | 130
2023-05-27 21:00 | Western | 1 | Gas | 943
2023-05-27 21:00 | Western | 2 | HFO | 661
2023-05-27 21:00 | Western | 3 | HSD | 0
2023-05-27 21:00 | Western | 6 | Coal | 2114
2023-05-27 21:00 | Western | 8 | HVDC | 904
2023-05-27 22:00 | Eastern | 1 | Gas | 5373.79
2023-05-27 22:00 | Eastern | 2 | HFO | 2306
2023-05-27 22:00 | Eastern | 5 | Hydro | 25
2023-05-27 22:00 | Eastern | 10 | Tripura | 140
2023-05-27 22:00 | Western | 1 | Gas | 945
2023-05-27 22:00 | Western | 2 | HFO | 649
2023-05-27 22:00 | Western | 3 | HSD | 0
2023-05-27 22:00 | Western | 6 | Coal | 2114
2023-05-27 22:00 | Western | 8 | HVDC | 831
2023-05-27 23:00 | Eastern | 1 | Gas | 5679.79
2023-05-27 23:00 | Eastern | 2 | HFO | 1767
2023-05-27 23:00 | Eastern | 5 | Hydro | 0
2023-05-27 23:00 | Eastern | 10 | Tripura | 140
2023-05-27 23:00 | Western | 1 | Gas | 960
2023-05-27 23:00 | Western | 2 | HFO | 620
2023-05-27 23:00 | Western | 3 | HSD | 0
2023-05-27 23:00 | Western | 6 | Coal | 2122
2023-05-27 23:00 | Western | 8 | HVDC | 836
2023-05-28 | Eastern | 1 | Gas | 5629.79
2023-05-28 | Eastern | 2 | HFO | 1443
2023-05-28 | Eastern | 10 | Tripura | 140
2023-05-28 | Eastern | 11 | Solar | 0
2023-05-28 | Western | 1 | Gas | 944
2023-05-28 | Western | 2 | HFO | 660
2023-05-28 | Western | 3 | HSD | 0
2023-05-28 | Western | 6 | Coal | 2153
2023-05-28 | Western | 8 | HVDC | 839
2023-05-28 01:00 | Eastern | 1 | Gas | 5581.79
2023-05-28 01:00 | Eastern | 2 | HFO | 1257
2023-05-28 01:00 | Eastern | 10 | Tripura | 136
2023-05-28 01:00 | Western | 1 | Gas | 931
2023-05-28 01:00 | Western | 2 | HFO | 580
2023-05-28 01:00 | Western | 3 | HSD | 0
2023-05-28 01:00 | Western | 6 | Coal | 2045
2023-05-28 01:00 | Western | 8 | HVDC | 902
2023-05-28 02:00 | Eastern | 1 | Gas | 5596.79
2023-05-28 02:00 | Eastern | 2 | HFO | 1056
2023-05-28 02:00 | Eastern | 10 | Tripura | 134
2023-05-28 02:00 | Western | 1 | Gas | 944
2023-05-28 02:00 | Western | 2 | HFO | 217.5
2023-05-28 02:00 | Western | 3 | HSD | 0
2023-05-28 02:00 | Western | 6 | Coal | 1998
2023-05-28 02:00 | Western | 8 | HVDC | 911
2023-05-28 03:00 | Eastern | 1 | Gas | 5582.79
2023-05-28 03:00 | Eastern | 2 | HFO | 842
2023-05-28 03:00 | Eastern | 10 | Tripura | 130
2023-05-28 03:00 | Western | 1 | Gas | 944
2023-05-28 03:00 | Western | 2 | HFO | 60.9
2023-05-28 03:00 | Western | 3 | HSD | 0
2023-05-28 03:00 | Western | 6 | Coal | 1956
2023-05-28 03:00 | Western | 8 | HVDC | 912
2023-05-28 04:00 | Eastern | 1 | Gas | 5557.79
2023-05-28 04:00 | Eastern | 2 | HFO | 754
2023-05-28 04:00 | Eastern | 10 | Tripura | 128
2023-05-28 04:00 | Western | 1 | Gas | 944
2023-05-28 04:00 | Western | 2 | HFO | 25.9
2023-05-28 04:00 | Western | 3 | HSD | 0
2023-05-28 04:00 | Western | 6 | Coal | 1838
2023-05-28 04:00 | Western | 8 | HVDC | 911
2023-05-28 05:00 | Eastern | 1 | Gas | 5433.79
2023-05-28 05:00 | Eastern | 2 | HFO | 687
2023-05-28 05:00 | Eastern | 10 | Tripura | 114
2023-05-28 05:00 | Eastern | 11 | Solar | 0
2023-05-28 05:00 | Western | 1 | Gas | 955
2023-05-28 05:00 | Western | 2 | HFO | 8.9
2023-05-28 05:00 | Western | 3 | HSD | 0
2023-05-28 05:00 | Western | 6 | Coal | 1800
2023-05-28 05:00 | Western | 8 | HVDC | 911
2023-05-28 05:00 | Western | 11 | Solar | 0
2023-05-28 06:00 | Eastern | 1 | Gas | 5250.79
2023-05-28 06:00 | Eastern | 2 | HFO | 628
2023-05-28 06:00 | Eastern | 10 | Tripura | 108
2023-05-28 06:00 | Eastern | 11 | Solar | 5
2023-05-28 06:00 | Western | 1 | Gas | 948
2023-05-28 06:00 | Western | 2 | HFO | 8.9
2023-05-28 06:00 | Western | 3 | HSD | 0
2023-05-28 06:00 | Western | 6 | Coal | 1772
2023-05-28 06:00 | Western | 8 | HVDC | 910
2023-05-28 06:00 | Western | 11 | Solar | 20.28
2023-05-28 07:00 | Eastern | 1 | Gas | 5411.79
2023-05-28 07:00 | Eastern | 2 | HFO | 646
2023-05-28 07:00 | Eastern | 10 | Tripura | 120
2023-05-28 07:00 | Eastern | 11 | Solar | 21
2023-05-28 07:00 | Western | 1 | Gas | 931
2023-05-28 07:00 | Western | 2 | HFO | 8.9
2023-05-28 07:00 | Western | 3 | HSD | 0
2023-05-28 07:00 | Western | 6 | Coal | 1772
2023-05-28 07:00 | Western | 8 | HVDC | 913
2023-05-28 07:00 | Western | 11 | Solar | 82
2023-05-28 08:00 | Eastern | 1 | Gas | 5372.79
2023-05-28 08:00 | Eastern | 2 | HFO | 763
2023-05-28 08:00 | Eastern | 10 | Tripura | 126
2023-05-28 08:00 | Eastern | 11 | Solar | 55
2023-05-28 08:00 | Western | 1 | Gas | 895
2023-05-28 08:00 | Western | 3 | HSD | 0
2023-05-28 08:00 | Western | 6 | Coal | 1910
2023-05-28 08:00 | Western | 8 | HVDC | 913
2023-05-28 08:00 | Western | 11 | Solar | 174.43
2023-05-28 09:00 | Eastern | 1 | Gas | 5508.79
2023-05-28 09:00 | Eastern | 2 | HFO | 925
2023-05-28 09:00 | Eastern | 10 | Tripura | 130
2023-05-28 09:00 | Eastern | 11 | Solar | 64
2023-05-28 09:00 | Western | 1 | Gas | 863
2023-05-28 09:00 | Western | 2 | HFO | 106
2023-05-28 09:00 | Western | 3 | HSD | 17
2023-05-28 09:00 | Western | 6 | Coal | 1906
2023-05-28 09:00 | Western | 8 | HVDC | 913
2023-05-28 09:00 | Western | 11 | Solar | 241.91
2023-05-28 10:00 | Eastern | 1 | Gas | 5502.79
2023-05-28 10:00 | Eastern | 2 | HFO | 1042
2023-05-28 10:00 | Eastern | 3 | HSD | 238
2023-05-28 10:00 | Eastern | 5 | Hydro | 0
2023-05-28 10:00 | Eastern | 10 | Tripura | 156
2023-05-28 10:00 | Eastern | 11 | Solar | 82
2023-05-28 10:00 | Western | 1 | Gas | 848
2023-05-28 10:00 | Western | 2 | HFO | 352
2023-05-28 10:00 | Western | 3 | HSD | 51
2023-05-28 10:00 | Western | 6 | Coal | 1864
2023-05-28 10:00 | Western | 8 | HVDC | 913
2023-05-28 10:00 | Western | 11 | Solar | 191.5
2023-05-28 11:00 | Eastern | 1 | Gas | 5399.79
2023-05-28 11:00 | Eastern | 2 | HFO | 1111
2023-05-28 11:00 | Eastern | 3 | HSD | 323
2023-05-28 11:00 | Eastern | 5 | Hydro | 25
2023-05-28 11:00 | Eastern | 10 | Tripura | 156
2023-05-28 11:00 | Eastern | 11 | Solar | 99
2023-05-28 11:00 | Western | 1 | Gas | 833
2023-05-28 11:00 | Western | 2 | HFO | 463
2023-05-28 11:00 | Western | 3 | HSD | 86
2023-05-28 11:00 | Western | 6 | Coal | 1857
2023-05-28 11:00 | Western | 8 | HVDC | 914
2023-05-28 11:00 | Western | 11 | Solar | 249.19
2023-05-28 12:00 | Eastern | 1 | Gas | 5502.79
2023-05-28 12:00 | Eastern | 2 | HFO | 1201
2023-05-28 12:00 | Eastern | 3 | HSD | 214
2023-05-28 12:00 | Eastern | 5 | Hydro | 25
2023-05-28 12:00 | Eastern | 10 | Tripura | 170
2023-05-28 12:00 | Eastern | 11 | Solar | 89
2023-05-28 12:00 | Western | 1 | Gas | 849
2023-05-28 12:00 | Western | 2 | HFO | 556
2023-05-28 12:00 | Western | 3 | HSD | 172
2023-05-28 12:00 | Western | 6 | Coal | 1807
2023-05-28 12:00 | Western | 8 | HVDC | 913
2023-05-28 12:00 | Western | 11 | Solar | 300.2
2023-05-28 13:00 | Eastern | 1 | Gas | 5391.79
2023-05-28 13:00 | Eastern | 2 | HFO | 1202
2023-05-28 13:00 | Eastern | 3 | HSD | 334
2023-05-28 13:00 | Eastern | 5 | Hydro | 25
2023-05-28 13:00 | Eastern | 10 | Tripura | 172
2023-05-28 13:00 | Eastern | 11 | Solar | 88
2023-05-28 13:00 | Western | 1 | Gas | 884
2023-05-28 13:00 | Western | 2 | HFO | 623
2023-05-28 13:00 | Western | 3 | HSD | 210
2023-05-28 13:00 | Western | 6 | Coal | 1859
2023-05-28 13:00 | Western | 8 | HVDC | 912
2023-05-28 13:00 | Western | 11 | Solar | 334.1
2023-05-28 14:00 | Eastern | 1 | Gas | 5363.79
2023-05-28 14:00 | Eastern | 2 | HFO | 1233
2023-05-28 14:00 | Eastern | 3 | HSD | 327
2023-05-28 14:00 | Eastern | 5 | Hydro | 25
2023-05-28 14:00 | Eastern | 10 | Tripura | 152
2023-05-28 14:00 | Eastern | 11 | Solar | 83
2023-05-28 14:00 | Western | 1 | Gas | 886
2023-05-28 14:00 | Western | 2 | HFO | 658
2023-05-28 14:00 | Western | 3 | HSD | 259
2023-05-28 14:00 | Western | 6 | Coal | 1836
2023-05-28 14:00 | Western | 8 | HVDC | 914
2023-05-28 14:00 | Western | 11 | Solar | 289.54
2023-05-28 15:00 | Eastern | 1 | Gas | 5413.29
2023-05-28 15:00 | Eastern | 2 | HFO | 1251
2023-05-28 15:00 | Eastern | 3 | HSD | 477
2023-05-28 15:00 | Eastern | 5 | Hydro | 25
2023-05-28 15:00 | Eastern | 10 | Tripura | 174
2023-05-28 15:00 | Eastern | 11 | Solar | 76
2023-05-28 15:00 | Western | 1 | Gas | 835
2023-05-28 15:00 | Western | 2 | HFO | 692
2023-05-28 15:00 | Western | 3 | HSD | 281
2023-05-28 15:00 | Western | 6 | Coal | 1871
2023-05-28 15:00 | Western | 8 | HVDC | 912
2023-05-28 15:00 | Western | 11 | Solar | 207.77
2023-05-28 16:00 | Eastern | 1 | Gas | 5395.29
2023-05-28 16:00 | Eastern | 2 | HFO | 1248
2023-05-28 16:00 | Eastern | 3 | HSD | 443
2023-05-28 16:00 | Eastern | 5 | Hydro | 25
2023-05-28 16:00 | Eastern | 10 | Tripura | 180
2023-05-28 16:00 | Eastern | 11 | Solar | 54
2023-05-28 16:00 | Western | 1 | Gas | 783
2023-05-28 16:00 | Western | 2 | HFO | 630
2023-05-28 16:00 | Western | 3 | HSD | 350
2023-05-28 16:00 | Western | 6 | Coal | 1864
2023-05-28 16:00 | Western | 8 | HVDC | 912
2023-05-28 16:00 | Western | 11 | Solar | 163.53
2023-05-28 17:00 | Eastern | 1 | Gas | 5394.79
2023-05-28 17:00 | Eastern | 2 | HFO | 1316
2023-05-28 17:00 | Eastern | 3 | HSD | 182
2023-05-28 17:00 | Eastern | 5 | Hydro | 25
2023-05-28 17:00 | Eastern | 10 | Tripura | 164
2023-05-28 17:00 | Eastern | 11 | Solar | 23
2023-05-28 17:00 | Western | 1 | Gas | 826
2023-05-28 17:00 | Western | 2 | HFO | 652
2023-05-28 17:00 | Western | 3 | HSD | 351
2023-05-28 17:00 | Western | 6 | Coal | 1903
2023-05-28 17:00 | Western | 8 | HVDC | 911
2023-05-28 17:00 | Western | 11 | Solar | 90.15
2023-05-28 18:00 | Eastern | 1 | Gas | 4911
2023-05-28 18:00 | Eastern | 2 | HFO | 1730
2023-05-28 18:00 | Eastern | 3 | HSD | 25
2023-05-28 18:00 | Eastern | 5 | Hydro | 25
2023-05-28 18:00 | Eastern | 10 | Tripura | 148
2023-05-28 18:00 | Eastern | 11 | Solar | 6
2023-05-28 18:00 | Western | 1 | Gas | 892
2023-05-28 18:00 | Western | 2 | HFO | 743
2023-05-28 18:00 | Western | 3 | HSD | 351
2023-05-28 18:00 | Western | 6 | Coal | 1820
2023-05-28 18:00 | Western | 8 | HVDC | 911
2023-05-28 18:00 | Western | 11 | Solar | 21.28
2023-05-28 19:00 | Eastern | 1 | Gas | 5431.79
2023-05-28 19:00 | Eastern | 2 | HFO | 2425
2023-05-28 19:00 | Eastern | 3 | HSD | 269
2023-05-28 19:00 | Eastern | 5 | Hydro | 25
2023-05-28 19:00 | Eastern | 10 | Tripura | 164
2023-05-28 19:00 | Western | 1 | Gas | 999
2023-05-28 19:00 | Western | 2 | HFO | 936
2023-05-28 19:00 | Western | 3 | HSD | 350
2023-05-28 19:00 | Western | 6 | Coal | 1834
2023-05-28 19:00 | Western | 8 | HVDC | 913
2023-05-28 19:00 | Western | 11 | Solar | 0
2023-05-28 19:30 | Eastern | 1 | Gas | 5506.79
2023-05-28 19:30 | Eastern | 2 | HFO | 2681
2023-05-28 19:30 | Eastern | 3 | HSD | 445
2023-05-28 19:30 | Eastern | 5 | Hydro | 25
2023-05-28 19:30 | Eastern | 10 | Tripura | 154
2023-05-28 19:30 | Western | 1 | Gas | 1008
2023-05-28 19:30 | Western | 2 | HFO | 1017
2023-05-28 19:30 | Western | 3 | HSD | 356
2023-05-28 19:30 | Western | 6 | Coal | 1986
2023-05-28 19:30 | Western | 8 | HVDC | 913
2023-05-28 20:00 | Eastern | 1 | Gas | 5492.79
2023-05-28 20:00 | Eastern | 2 | HFO | 2723
2023-05-28 20:00 | Eastern | 3 | HSD | 175
2023-05-28 20:00 | Eastern | 5 | Hydro | 25
2023-05-28 20:00 | Eastern | 10 | Tripura | 158
2023-05-28 20:00 | Western | 1 | Gas | 1007
2023-05-28 20:00 | Western | 2 | HFO | 1037
2023-05-28 20:00 | Western | 3 | HSD | 356
2023-05-28 20:00 | Western | 6 | Coal | 2047
2023-05-28 20:00 | Western | 8 | HVDC | 913
2023-05-28 21:00 | Eastern | 1 | Gas | 5551.79
2023-05-28 21:00 | Eastern | 2 | HFO | 2898
2023-05-28 21:00 | Eastern | 3 | HSD | 230
2023-05-28 21:00 | Eastern | 5 | Hydro | 25
2023-05-28 21:00 | Eastern | 10 | Tripura | 166
2023-05-28 21:00 | Western | 1 | Gas | 1009
2023-05-28 21:00 | Western | 2 | HFO | 1032
2023-05-28 21:00 | Western | 3 | HSD | 142
2023-05-28 21:00 | Western | 6 | Coal | 2170
2023-05-28 21:00 | Western | 8 | HVDC | 913
2023-05-28 22:00 | Eastern | 1 | Gas | 5623.79
2023-05-28 22:00 | Eastern | 2 | HFO | 2758
2023-05-28 22:00 | Eastern | 3 | HSD | 229
2023-05-28 22:00 | Eastern | 5 | Hydro | 25
2023-05-28 22:00 | Eastern | 10 | Tripura | 156
2023-05-28 22:00 | Western | 1 | Gas | 1021
2023-05-28 22:00 | Western | 2 | HFO | 1023
2023-05-28 22:00 | Western | 6 | Coal | 2177
2023-05-28 22:00 | Western | 8 | HVDC | 913
2023-05-28 23:00 | Eastern | 1 | Gas | 5640.79
2023-05-28 23:00 | Eastern | 2 | HFO | 2216
2023-05-28 23:00 | Eastern | 3 | HSD | 435
2023-05-28 23:00 | Eastern | 5 | Hydro | 0
2023-05-28 23:00 | Eastern | 10 | Tripura | 150
2023-05-28 23:00 | Western | 1 | Gas | 1026
2023-05-28 23:00 | Western | 2 | HFO | 932
2023-05-28 23:00 | Western | 6 | Coal | 2175
2023-05-28 23:00 | Western | 8 | HVDC | 911
2023-05-29 | Eastern | 1 | Gas | 5573.79
2023-05-29 | Eastern | 2 | HFO | 1692
2023-05-29 | Eastern | 3 | HSD | 437
2023-05-29 | Eastern | 10 | Tripura | 160
2023-05-29 | Eastern | 11 | Solar | 0
2023-05-29 | Western | 1 | Gas | 1027
2023-05-29 | Western | 2 | HFO | 917
2023-05-29 | Western | 6 | Coal | 2166
2023-05-29 | Western | 8 | HVDC | 913
2023-05-29 | Western | 11 | Solar | 0
2023-05-29 01:00 | Eastern | 1 | Gas | 5631.79
2023-05-29 01:00 | Eastern | 2 | HFO | 1273
2023-05-29 01:00 | Eastern | 3 | HSD | 437
2023-05-29 01:00 | Eastern | 10 | Tripura | 164
2023-05-29 01:00 | Western | 1 | Gas | 1024
2023-05-29 01:00 | Western | 2 | HFO | 661
2023-05-29 01:00 | Western | 6 | Coal | 2170
2023-05-29 01:00 | Western | 8 | HVDC | 915
2023-05-29 02:00 | Eastern | 1 | Gas | 5589.79
2023-05-29 02:00 | Eastern | 2 | HFO | 1197
2023-05-29 02:00 | Eastern | 3 | HSD | 388
2023-05-29 02:00 | Eastern | 10 | Tripura | 152
2023-05-29 02:00 | Western | 1 | Gas | 1030
2023-05-29 02:00 | Western | 2 | HFO | 644
2023-05-29 02:00 | Western | 6 | Coal | 2180
2023-05-29 02:00 | Western | 8 | HVDC | 914
2023-05-29 03:00 | Eastern | 1 | Gas | 5554.79
2023-05-29 03:00 | Eastern | 2 | HFO | 1178
2023-05-29 03:00 | Eastern | 3 | HSD | 247
2023-05-29 03:00 | Eastern | 10 | Tripura | 150
2023-05-29 03:00 | Western | 1 | Gas | 1029
2023-05-29 03:00 | Western | 2 | HFO | 603
2023-05-29 03:00 | Western | 6 | Coal | 2101
2023-05-29 03:00 | Western | 8 | HVDC | 915
2023-05-29 04:00 | Eastern | 1 | Gas | 5581.79
2023-05-29 04:00 | Eastern | 2 | HFO | 1179
2023-05-29 04:00 | Eastern | 3 | HSD | 155
2023-05-29 04:00 | Eastern | 10 | Tripura | 154
2023-05-29 04:00 | Western | 1 | Gas | 1043
2023-05-29 04:00 | Western | 2 | HFO | 556
2023-05-29 04:00 | Western | 6 | Coal | 2113
2023-05-29 04:00 | Western | 8 | HVDC | 913
2023-05-29 05:00 | Eastern | 1 | Gas | 5536.79
2023-05-29 05:00 | Eastern | 2 | HFO | 1186
2023-05-29 05:00 | Eastern | 10 | Tripura | 146
2023-05-29 05:00 | Western | 1 | Gas | 1046
2023-05-29 05:00 | Western | 2 | HFO | 507
2023-05-29 05:00 | Western | 6 | Coal | 2127
2023-05-29 05:00 | Western | 8 | HVDC | 913
2023-05-29 06:00 | Eastern | 1 | Gas | 5269
2023-05-29 06:00 | Eastern | 2 | HFO | 1172
2023-05-29 06:00 | Eastern | 10 | Tripura | 124
2023-05-29 06:00 | Eastern | 11 | Solar | 6
2023-05-29 06:00 | Western | 1 | Gas | 1044
2023-05-29 06:00 | Western | 2 | HFO | 403
2023-05-29 06:00 | Western | 6 | Coal | 2007
2023-05-29 06:00 | Western | 8 | HVDC | 914
2023-05-29 06:00 | Western | 11 | Solar | 21.28
2023-05-29 07:00 | Eastern | 1 | Gas | 5278
2023-05-29 07:00 | Eastern | 2 | HFO | 1157
2023-05-29 07:00 | Eastern | 10 | Tripura | 128
2023-05-29 07:00 | Eastern | 11 | Solar | 28
2023-05-29 07:00 | Western | 1 | Gas | 1032
2023-05-29 07:00 | Western | 2 | HFO | 409
2023-05-29 07:00 | Western | 6 | Coal | 2011
2023-05-29 07:00 | Western | 8 | HVDC | 914
2023-05-29 07:00 | Western | 11 | Solar | 90.04
2023-05-29 08:00 | Eastern | 1 | Gas | 5412.79
2023-05-29 08:00 | Eastern | 2 | HFO | 1082
2023-05-29 08:00 | Eastern | 10 | Tripura | 142
2023-05-29 08:00 | Eastern | 11 | Solar | 55
2023-05-29 08:00 | Western | 1 | Gas | 999
2023-05-29 08:00 | Western | 2 | HFO | 448
2023-05-29 08:00 | Western | 6 | Coal | 1991
2023-05-29 08:00 | Western | 8 | HVDC | 907
2023-05-29 08:00 | Western | 11 | Solar | 182.34
2023-05-29 09:00 | Eastern | 1 | Gas | 5442.79
2023-05-29 09:00 | Eastern | 2 | HFO | 1047
2023-05-29 09:00 | Eastern | 5 | Hydro | 0
2023-05-29 09:00 | Eastern | 10 | Tripura | 138
2023-05-29 09:00 | Eastern | 11 | Solar | 79
2023-05-29 09:00 | Western | 1 | Gas | 969
2023-05-29 09:00 | Western | 2 | HFO | 463
2023-05-29 09:00 | Western | 6 | Coal | 1947
2023-05-29 09:00 | Western | 8 | HVDC | 908
2023-05-29 09:00 | Western | 11 | Solar | 257.61
2023-05-29 10:00 | Eastern | 1 | Gas | 5277
2023-05-29 10:00 | Eastern | 2 | HFO | 1116
2023-05-29 10:00 | Eastern | 3 | HSD | 60
2023-05-29 10:00 | Eastern | 5 | Hydro | 25
2023-05-29 10:00 | Eastern | 10 | Tripura | 130
2023-05-29 10:00 | Eastern | 11 | Solar | 101
2023-05-29 10:00 | Western | 1 | Gas | 944
2023-05-29 10:00 | Western | 2 | HFO | 467
2023-05-29 10:00 | Western | 6 | Coal | 1920
2023-05-29 10:00 | Western | 8 | HVDC | 908
2023-05-29 10:00 | Western | 11 | Solar | 313.73
2023-05-29 11:00 | Eastern | 1 | Gas | 5276
2023-05-29 11:00 | Eastern | 2 | HFO | 1156
2023-05-29 11:00 | Eastern | 3 | HSD | 63
2023-05-29 11:00 | Eastern | 5 | Hydro | 25
2023-05-29 11:00 | Eastern | 10 | Tripura | 134
2023-05-29 11:00 | Eastern | 11 | Solar | 107
2023-05-29 11:00 | Western | 1 | Gas | 932
2023-05-29 11:00 | Western | 2 | HFO | 523
2023-05-29 11:00 | Western | 6 | Coal | 1939
2023-05-29 11:00 | Western | 8 | HVDC | 908
2023-05-29 11:00 | Western | 11 | Solar | 347.39
2023-05-29 12:00 | Eastern | 1 | Gas | 5464.79
2023-05-29 12:00 | Eastern | 2 | HFO | 1184
2023-05-29 12:00 | Eastern | 3 | HSD | 431
2023-05-29 12:00 | Eastern | 5 | Hydro | 25
2023-05-29 12:00 | Eastern | 10 | Tripura | 132
2023-05-29 12:00 | Eastern | 11 | Solar | 107
2023-05-29 12:00 | Western | 1 | Gas | 911
2023-05-29 12:00 | Western | 2 | HFO | 529
2023-05-29 12:00 | Western | 6 | Coal | 1908
2023-05-29 12:00 | Western | 8 | HVDC | 908
2023-05-29 12:00 | Western | 11 | Solar | 335.29
2023-05-29 13:00 | Eastern | 1 | Gas | 5375.79
2023-05-29 13:00 | Eastern | 2 | HFO | 1217
2023-05-29 13:00 | Eastern | 3 | HSD | 439
2023-05-29 13:00 | Eastern | 5 | Hydro | 25
2023-05-29 13:00 | Eastern | 10 | Tripura | 136
2023-05-29 13:00 | Eastern | 11 | Solar | 79
2023-05-29 13:00 | Western | 1 | Gas | 900
2023-05-29 13:00 | Western | 2 | HFO | 546
2023-05-29 13:00 | Western | 6 | Coal | 1962
2023-05-29 13:00 | Western | 8 | HVDC | 908
2023-05-29 13:00 | Western | 11 | Solar | 339.26
2023-05-29 14:00 | Eastern | 1 | Gas | 5379.79
2023-05-29 14:00 | Eastern | 2 | HFO | 1183
2023-05-29 14:00 | Eastern | 3 | HSD | 394
2023-05-29 14:00 | Eastern | 5 | Hydro | 25
2023-05-29 14:00 | Eastern | 10 | Tripura | 138
2023-05-29 14:00 | Eastern | 11 | Solar | 90
2023-05-29 14:00 | Western | 1 | Gas | 897
2023-05-29 14:00 | Western | 2 | HFO | 564
2023-05-29 14:00 | Western | 6 | Coal | 1985
2023-05-29 14:00 | Western | 8 | HVDC | 908
2023-05-29 14:00 | Western | 11 | Solar | 286.29
2023-05-29 15:00 | Eastern | 1 | Gas | 5304.79
2023-05-29 15:00 | Eastern | 2 | HFO | 1169
2023-05-29 15:00 | Eastern | 3 | HSD | 309
2023-05-29 15:00 | Eastern | 5 | Hydro | 25
2023-05-29 15:00 | Eastern | 10 | Tripura | 168
2023-05-29 15:00 | Eastern | 11 | Solar | 79
2023-05-29 15:00 | Western | 1 | Gas | 887
2023-05-29 15:00 | Western | 2 | HFO | 584
2023-05-29 15:00 | Western | 6 | Coal | 2041
2023-05-29 15:00 | Western | 8 | HVDC | 908
2023-05-29 15:00 | Western | 11 | Solar | 243.76
2023-05-29 16:00 | Eastern | 1 | Gas | 5335.79
2023-05-29 16:00 | Eastern | 2 | HFO | 1176
2023-05-29 16:00 | Eastern | 3 | HSD | 235
2023-05-29 16:00 | Eastern | 5 | Hydro | 25
2023-05-29 16:00 | Eastern | 10 | Tripura | 160
2023-05-29 16:00 | Eastern | 11 | Solar | 52
2023-05-29 16:00 | Western | 1 | Gas | 895
2023-05-29 16:00 | Western | 2 | HFO | 559
2023-05-29 16:00 | Western | 6 | Coal | 2064
2023-05-29 16:00 | Western | 8 | HVDC | 908
2023-05-29 16:00 | Western | 11 | Solar | 165.2
2023-05-29 17:00 | Eastern | 1 | Gas | 5377.79
2023-05-29 17:00 | Eastern | 2 | HFO | 1255
2023-05-29 17:00 | Eastern | 3 | HSD | 310
2023-05-29 17:00 | Eastern | 5 | Hydro | 25
2023-05-29 17:00 | Eastern | 10 | Tripura | 148
2023-05-29 17:00 | Eastern | 11 | Solar | 25
2023-05-29 17:00 | Western | 1 | Gas | 893
2023-05-29 17:00 | Western | 2 | HFO | 598
2023-05-29 17:00 | Western | 6 | Coal | 2016
2023-05-29 17:00 | Western | 8 | HVDC | 908
2023-05-29 17:00 | Western | 11 | Solar | 89.16
2023-05-29 18:00 | Eastern | 1 | Gas | 5062
2023-05-29 18:00 | Eastern | 2 | HFO | 1612
2023-05-29 18:00 | Eastern | 3 | HSD | 81
2023-05-29 18:00 | Eastern | 5 | Hydro | 25
2023-05-29 18:00 | Eastern | 10 | Tripura | 150
2023-05-29 18:00 | Eastern | 11 | Solar | 5
2023-05-29 18:00 | Western | 1 | Gas | 903
2023-05-29 18:00 | Western | 2 | HFO | 711
2023-05-29 18:00 | Western | 6 | Coal | 1975
2023-05-29 18:00 | Western | 8 | HVDC | 907
2023-05-29 18:00 | Western | 11 | Solar | 19.23
2023-05-29 19:00 | Eastern | 1 | Gas | 5322
2023-05-29 19:00 | Eastern | 2 | HFO | 2736
2023-05-29 19:00 | Eastern | 3 | HSD | 148
2023-05-29 19:00 | Eastern | 5 | Hydro | 25
2023-05-29 19:00 | Eastern | 10 | Tripura | 160
2023-05-29 19:00 | Eastern | 11 | Solar | 0
2023-05-29 19:00 | Western | 1 | Gas | 913
2023-05-29 19:00 | Western | 2 | HFO | 969
2023-05-29 19:00 | Western | 6 | Coal | 2079
2023-05-29 19:00 | Western | 8 | HVDC | 907
2023-05-29 19:00 | Western | 11 | Solar | 0
2023-05-29 19:30 | Eastern | 1 | Gas | 5413.79
2023-05-29 19:30 | Eastern | 2 | HFO | 2919
2023-05-29 19:30 | Eastern | 3 | HSD | 151
2023-05-29 19:30 | Eastern | 5 | Hydro | 25
2023-05-29 19:30 | Eastern | 10 | Tripura | 156
2023-05-29 19:30 | Western | 1 | Gas | 913
2023-05-29 19:30 | Western | 2 | HFO | 1007
2023-05-29 19:30 | Western | 6 | Coal | 2220
2023-05-29 19:30 | Western | 8 | HVDC | 908
2023-05-29 20:00 | Eastern | 1 | Gas | 5469.79
2023-05-29 20:00 | Eastern | 2 | HFO | 3018
2023-05-29 20:00 | Eastern | 3 | HSD | 248
2023-05-29 20:00 | Eastern | 5 | Hydro | 25
2023-05-29 20:00 | Eastern | 10 | Tripura | 154
2023-05-29 20:00 | Western | 1 | Gas | 930
2023-05-29 20:00 | Western | 2 | HFO | 1020
2023-05-29 20:00 | Western | 6 | Coal | 2272
2023-05-29 20:00 | Western | 8 | HVDC | 909
2023-05-29 21:00 | Eastern | 1 | Gas | 5536.79
2023-05-29 21:00 | Eastern | 2 | HFO | 3039
2023-05-29 21:00 | Eastern | 3 | HSD | 440
2023-05-29 21:00 | Eastern | 5 | Hydro | 25
2023-05-29 21:00 | Eastern | 10 | Tripura | 156
2023-05-29 21:00 | Western | 1 | Gas | 940
2023-05-29 21:00 | Western | 2 | HFO | 1022
2023-05-29 21:00 | Western | 6 | Coal | 2280
2023-05-29 21:00 | Western | 8 | HVDC | 898
2023-05-29 22:00 | Eastern | 1 | Gas | 5456.79
2023-05-29 22:00 | Eastern | 2 | HFO | 2578
2023-05-29 22:00 | Eastern | 3 | HSD | 440
2023-05-29 22:00 | Eastern | 5 | Hydro | 25
2023-05-29 22:00 | Eastern | 10 | Tripura | 164
2023-05-29 22:00 | Western | 1 | Gas | 950
2023-05-29 22:00 | Western | 2 | HFO | 1018
2023-05-29 22:00 | Western | 6 | Coal | 2268
2023-05-29 22:00 | Western | 8 | HVDC | 812
2023-05-29 23:00 | Eastern | 1 | Gas | 5426.79
2023-05-29 23:00 | Eastern | 2 | HFO | 2023
2023-05-29 23:00 | Eastern | 3 | HSD | 383
2023-05-29 23:00 | Eastern | 5 | Hydro | 0
2023-05-29 23:00 | Eastern | 10 | Tripura | 168
2023-05-29 23:00 | Western | 1 | Gas | 961
2023-05-29 23:00 | Western | 2 | HFO | 958
2023-05-29 23:00 | Western | 6 | Coal | 2281
2023-05-29 23:00 | Western | 8 | HVDC | 813
2023-05-30 | Eastern | 1 | Gas | 5546.79
2023-05-30 | Eastern | 2 | HFO | 1528
2023-05-30 | Eastern | 3 | HSD | 337
2023-05-30 | Eastern | 10 | Tripura | 168
2023-05-30 | Eastern | 11 | Solar | 0
2023-05-30 | Western | 1 | Gas | 982
2023-05-30 | Western | 2 | HFO | 891
2023-05-30 | Western | 6 | Coal | 2277
2023-05-30 | Western | 8 | HVDC | 814
2023-05-30 01:00 | Eastern | 1 | Gas | 5569.79
2023-05-30 01:00 | Eastern | 2 | HFO | 1289
2023-05-30 01:00 | Eastern | 3 | HSD | 396
2023-05-30 01:00 | Eastern | 10 | Tripura | 168
2023-05-30 01:00 | Eastern | 12 | Wind | 0
2023-05-30 01:00 | Western | 1 | Gas | 1008
2023-05-30 01:00 | Western | 2 | HFO | 687
2023-05-30 01:00 | Western | 6 | Coal | 2277
2023-05-30 01:00 | Western | 8 | HVDC | 862
2023-05-30 02:00 | Eastern | 1 | Gas | 5580.79
2023-05-30 02:00 | Eastern | 2 | HFO | 1193
2023-05-30 02:00 | Eastern | 3 | HSD | 396
2023-05-30 02:00 | Eastern | 10 | Tripura | 162
2023-05-30 02:00 | Eastern | 12 | Wind | 0
2023-05-30 02:00 | Western | 1 | Gas | 1027
2023-05-30 02:00 | Western | 2 | HFO | 644
2023-05-30 02:00 | Western | 6 | Coal | 2270
2023-05-30 02:00 | Western | 8 | HVDC | 861
2023-05-30 03:00 | Eastern | 1 | Gas | 5480.79
2023-05-30 03:00 | Eastern | 2 | HFO | 1147
2023-05-30 03:00 | Eastern | 3 | HSD | 370
2023-05-30 03:00 | Eastern | 10 | Tripura | 164
2023-05-30 03:00 | Eastern | 12 | Wind | 0
2023-05-30 03:00 | Western | 1 | Gas | 1049
2023-05-30 03:00 | Western | 2 | HFO | 580
2023-05-30 03:00 | Western | 6 | Coal | 2276
2023-05-30 03:00 | Western | 8 | HVDC | 908
2023-05-30 04:00 | Eastern | 1 | Gas | 5478.79
2023-05-30 04:00 | Eastern | 2 | HFO | 1156
2023-05-30 04:00 | Eastern | 3 | HSD | 345
2023-05-30 04:00 | Eastern | 10 | Tripura | 158
2023-05-30 04:00 | Eastern | 12 | Wind | 0
2023-05-30 04:00 | Western | 1 | Gas | 1074
2023-05-30 04:00 | Western | 2 | HFO | 559
2023-05-30 04:00 | Western | 6 | Coal | 2279
2023-05-30 04:00 | Western | 8 | HVDC | 910
2023-05-30 05:00 | Eastern | 1 | Gas | 5436.79
2023-05-30 05:00 | Eastern | 2 | HFO | 1151
2023-05-30 05:00 | Eastern | 3 | HSD | 264
2023-05-30 05:00 | Eastern | 10 | Tripura | 144
2023-05-30 05:00 | Eastern | 11 | Solar | 0
2023-05-30 05:00 | Eastern | 12 | Wind | 0
2023-05-30 05:00 | Western | 1 | Gas | 1090
2023-05-30 05:00 | Western | 2 | HFO | 486
2023-05-30 05:00 | Western | 6 | Coal | 2277
2023-05-30 05:00 | Western | 8 | HVDC | 910
2023-05-30 05:00 | Western | 11 | Solar | 0
2023-05-30 06:00 | Eastern | 1 | Gas | 5348.79
2023-05-30 06:00 | Eastern | 2 | HFO | 1158
2023-05-30 06:00 | Eastern | 3 | HSD | 0
2023-05-30 06:00 | Eastern | 10 | Tripura | 134
2023-05-30 06:00 | Eastern | 11 | Solar | 6
2023-05-30 06:00 | Eastern | 12 | Wind | 0
2023-05-30 06:00 | Western | 1 | Gas | 1051
2023-05-30 06:00 | Western | 2 | HFO | 482
2023-05-30 06:00 | Western | 6 | Coal | 2278
2023-05-30 06:00 | Western | 8 | HVDC | 910
2023-05-30 06:00 | Western | 11 | Solar | 22.3
2023-05-30 07:00 | Eastern | 1 | Gas | 5132
2023-05-30 07:00 | Eastern | 2 | HFO | 1145
2023-05-30 07:00 | Eastern | 10 | Tripura | 132
2023-05-30 07:00 | Eastern | 11 | Solar | 27
2023-05-30 07:00 | Eastern | 12 | Wind | 0
2023-05-30 07:00 | Western | 1 | Gas | 1091
2023-05-30 07:00 | Western | 2 | HFO | 515
2023-05-30 07:00 | Western | 6 | Coal | 2265
2023-05-30 07:00 | Western | 8 | HVDC | 910
2023-05-30 07:00 | Western | 11 | Solar | 89.02
2023-05-30 08:00 | Eastern | 1 | Gas | 5289
2023-05-30 08:00 | Eastern | 2 | HFO | 1112
2023-05-30 08:00 | Eastern | 10 | Tripura | 136
2023-05-30 08:00 | Eastern | 11 | Solar | 48
2023-05-30 08:00 | Eastern | 12 | Wind | 0
2023-05-30 08:00 | Western | 1 | Gas | 1069
2023-05-30 08:00 | Western | 2 | HFO | 509
2023-05-30 08:00 | Western | 6 | Coal | 2228
2023-05-30 08:00 | Western | 8 | HVDC | 912
2023-05-30 08:00 | Western | 11 | Solar | 148.23
2023-05-30 09:00 | Eastern | 1 | Gas | 5250
2023-05-30 09:00 | Eastern | 2 | HFO | 1017
2023-05-30 09:00 | Eastern | 5 | Hydro | 0
2023-05-30 09:00 | Eastern | 10 | Tripura | 142
2023-05-30 09:00 | Eastern | 11 | Solar | 80
2023-05-30 09:00 | Eastern | 12 | Wind | 0
2023-05-30 09:00 | Western | 1 | Gas | 1055
2023-05-30 09:00 | Western | 2 | HFO | 513
2023-05-30 09:00 | Western | 6 | Coal | 2256
2023-05-30 09:00 | Western | 8 | HVDC | 912
2023-05-30 09:00 | Western | 11 | Solar | 215.37
2023-05-30 10:00 | Eastern | 1 | Gas | 4974
2023-05-30 10:00 | Eastern | 2 | HFO | 1056
2023-05-30 10:00 | Eastern | 5 | Hydro | 25
2023-05-30 10:00 | Eastern | 10 | Tripura | 130
2023-05-30 10:00 | Eastern | 11 | Solar | 91
2023-05-30 10:00 | Eastern | 12 | Wind | 0
2023-05-30 10:00 | Western | 1 | Gas | 1010
2023-05-30 10:00 | Western | 2 | HFO | 468
2023-05-30 10:00 | Western | 6 | Coal | 2258
2023-05-30 10:00 | Western | 8 | HVDC | 913
2023-05-30 10:00 | Western | 11 | Solar | 298.95
2023-05-30 11:00 | Eastern | 1 | Gas | 5030
2023-05-30 11:00 | Eastern | 2 | HFO | 1113
2023-05-30 11:00 | Eastern | 5 | Hydro | 25
2023-05-30 11:00 | Eastern | 10 | Tripura | 128
2023-05-30 11:00 | Eastern | 11 | Solar | 87
2023-05-30 11:00 | Eastern | 12 | Wind | 1
2023-05-30 11:00 | Western | 1 | Gas | 986
2023-05-30 11:00 | Western | 2 | HFO | 481
2023-05-30 11:00 | Western | 6 | Coal | 2286
2023-05-30 11:00 | Western | 8 | HVDC | 911
2023-05-30 11:00 | Western | 11 | Solar | 304.01
2023-05-30 12:00 | Eastern | 1 | Gas | 5285.79
2023-05-30 12:00 | Eastern | 2 | HFO | 1148
2023-05-30 12:00 | Eastern | 3 | HSD | 43
2023-05-30 12:00 | Eastern | 5 | Hydro | 25
2023-05-30 12:00 | Eastern | 10 | Tripura | 122
2023-05-30 12:00 | Eastern | 11 | Solar | 93
2023-05-30 12:00 | Eastern | 12 | Wind | 1
2023-05-30 12:00 | Western | 1 | Gas | 1049
2023-05-30 12:00 | Western | 2 | HFO | 502
2023-05-30 12:00 | Western | 6 | Coal | 2337
2023-05-30 12:00 | Western | 8 | HVDC | 911
2023-05-30 12:00 | Western | 11 | Solar | 334.41
2023-05-30 13:00 | Eastern | 1 | Gas | 5302.79
2023-05-30 13:00 | Eastern | 2 | HFO | 1151
2023-05-30 13:00 | Eastern | 3 | HSD | 397
2023-05-30 13:00 | Eastern | 5 | Hydro | 25
2023-05-30 13:00 | Eastern | 10 | Tripura | 124
2023-05-30 13:00 | Eastern | 11 | Solar | 79
2023-05-30 13:00 | Eastern | 12 | Wind | 2.01
2023-05-30 13:00 | Western | 1 | Gas | 1074
2023-05-30 13:00 | Western | 2 | HFO | 483
2023-05-30 13:00 | Western | 6 | Coal | 2323
2023-05-30 13:00 | Western | 8 | HVDC | 913
2023-05-30 13:00 | Western | 11 | Solar | 300.38
2023-05-30 14:00 | Eastern | 1 | Gas | 5341.79
2023-05-30 14:00 | Eastern | 2 | HFO | 1213
2023-05-30 14:00 | Eastern | 3 | HSD | 396
2023-05-30 14:00 | Eastern | 5 | Hydro | 25
2023-05-30 14:00 | Eastern | 10 | Tripura | 120
2023-05-30 14:00 | Eastern | 11 | Solar | 94
2023-05-30 14:00 | Eastern | 12 | Wind | 3.31
2023-05-30 14:00 | Western | 1 | Gas | 1061
2023-05-30 14:00 | Western | 2 | HFO | 509
2023-05-30 14:00 | Western | 6 | Coal | 2341
2023-05-30 14:00 | Western | 8 | HVDC | 912
2023-05-30 14:00 | Western | 11 | Solar | 267.71
2023-05-30 15:00 | Eastern | 1 | Gas | 5410.79
2023-05-30 15:00 | Eastern | 2 | HFO | 1204
2023-05-30 15:00 | Eastern | 3 | HSD | 396
2023-05-30 15:00 | Eastern | 5 | Hydro | 25
2023-05-30 15:00 | Eastern | 10 | Tripura | 138
2023-05-30 15:00 | Eastern | 11 | Solar | 80
2023-05-30 15:00 | Eastern | 12 | Wind | 2.9
2023-05-30 15:00 | Western | 1 | Gas | 1048
2023-05-30 15:00 | Western | 2 | HFO | 519
2023-05-30 15:00 | Western | 6 | Coal | 2325
2023-05-30 15:00 | Western | 8 | HVDC | 913
2023-05-30 15:00 | Western | 11 | Solar | 248.83
2023-05-30 16:00 | Eastern | 1 | Gas | 5399.79
2023-05-30 16:00 | Eastern | 2 | HFO | 1201
2023-05-30 16:00 | Eastern | 3 | HSD | 344
2023-05-30 16:00 | Eastern | 5 | Hydro | 25
2023-05-30 16:00 | Eastern | 10 | Tripura | 122
2023-05-30 16:00 | Eastern | 11 | Solar | 39
2023-05-30 16:00 | Eastern | 12 | Wind | 1.77
2023-05-30 16:00 | Western | 1 | Gas | 1034
2023-05-30 16:00 | Western | 2 | HFO | 498
2023-05-30 16:00 | Western | 6 | Coal | 2325
2023-05-30 16:00 | Western | 8 | HVDC | 913
2023-05-30 16:00 | Western | 11 | Solar | 175.54
2023-05-30 17:00 | Eastern | 1 | Gas | 5363.79
2023-05-30 17:00 | Eastern | 2 | HFO | 1288
2023-05-30 17:00 | Eastern | 3 | HSD | 0
2023-05-30 17:00 | Eastern | 5 | Hydro | 25
2023-05-30 17:00 | Eastern | 10 | Tripura | 130
2023-05-30 17:00 | Eastern | 11 | Solar | 19
2023-05-30 17:00 | Eastern | 12 | Wind | 0
2023-05-30 17:00 | Western | 1 | Gas | 1056
2023-05-30 17:00 | Western | 2 | HFO | 522
2023-05-30 17:00 | Western | 6 | Coal | 2329
2023-05-30 17:00 | Western | 8 | HVDC | 912
2023-05-30 17:00 | Western | 11 | Solar | 92.1
2023-05-30 18:00 | Eastern | 1 | Gas | 5260.79
2023-05-30 18:00 | Eastern | 2 | HFO | 1502
2023-05-30 18:00 | Eastern | 3 | HSD | 0
2023-05-30 18:00 | Eastern | 5 | Hydro | 25
2023-05-30 18:00 | Eastern | 10 | Tripura | 134
2023-05-30 18:00 | Eastern | 11 | Solar | 4
2023-05-30 18:00 | Eastern | 12 | Wind | 0
2023-05-30 18:00 | Western | 1 | Gas | 1061
2023-05-30 18:00 | Western | 2 | HFO | 612
2023-05-30 18:00 | Western | 3 | HSD | 0
2023-05-30 18:00 | Western | 6 | Coal | 2284
2023-05-30 18:00 | Western | 8 | HVDC | 913
2023-05-30 18:00 | Western | 11 | Solar | 24.23
2023-05-30 19:00 | Eastern | 1 | Gas | 5365
2023-05-30 19:00 | Eastern | 2 | HFO | 2628
2023-05-30 19:00 | Eastern | 3 | HSD | 254
2023-05-30 19:00 | Eastern | 5 | Hydro | 25
2023-05-30 19:00 | Eastern | 10 | Tripura | 144
2023-05-30 19:00 | Eastern | 11 | Solar | 0
2023-05-30 19:00 | Eastern | 12 | Wind | 1
2023-05-30 19:00 | Western | 1 | Gas | 1149
2023-05-30 19:00 | Western | 2 | HFO | 926
2023-05-30 19:00 | Western | 3 | HSD | 18
2023-05-30 19:00 | Western | 6 | Coal | 2207
2023-05-30 19:00 | Western | 8 | HVDC | 913
2023-05-30 19:00 | Western | 11 | Solar | 0
2023-05-30 19:30 | Eastern | 1 | Gas | 5549
2023-05-30 19:30 | Eastern | 2 | HFO | 2840
2023-05-30 19:30 | Eastern | 3 | HSD | 243
2023-05-30 19:30 | Eastern | 5 | Hydro | 25
2023-05-30 19:30 | Eastern | 10 | Tripura | 134
2023-05-30 19:30 | Eastern | 12 | Wind | 2
2023-05-30 19:30 | Western | 1 | Gas | 1172
2023-05-30 19:30 | Western | 2 | HFO | 971
2023-05-30 19:30 | Western | 3 | HSD | 15
2023-05-30 19:30 | Western | 6 | Coal | 2168
2023-05-30 19:30 | Western | 8 | HVDC | 913
2023-05-30 19:30 | Western | 11 | Solar | 0
2023-05-30 20:00 | Eastern | 1 | Gas | 5535
2023-05-30 20:00 | Eastern | 2 | HFO | 2895
2023-05-30 20:00 | Eastern | 3 | HSD | 243
2023-05-30 20:00 | Eastern | 5 | Hydro | 25
2023-05-30 20:00 | Eastern | 10 | Tripura | 136
2023-05-30 20:00 | Eastern | 12 | Wind | 4
2023-05-30 20:00 | Western | 1 | Gas | 1175
2023-05-30 20:00 | Western | 2 | HFO | 985
2023-05-30 20:00 | Western | 3 | HSD | 15
2023-05-30 20:00 | Western | 6 | Coal | 2262
2023-05-30 20:00 | Western | 8 | HVDC | 913
2023-05-30 21:00 | Eastern | 1 | Gas | 5619.79
2023-05-30 21:00 | Eastern | 2 | HFO | 2900
2023-05-30 21:00 | Eastern | 3 | HSD | 351
2023-05-30 21:00 | Eastern | 5 | Hydro | 25
2023-05-30 21:00 | Eastern | 10 | Tripura | 136
2023-05-30 21:00 | Eastern | 12 | Wind | 1
2023-05-30 21:00 | Western | 1 | Gas | 1186
2023-05-30 21:00 | Western | 2 | HFO | 1023
2023-05-30 21:00 | Western | 3 | HSD | 12
2023-05-30 21:00 | Western | 6 | Coal | 2345
2023-05-30 21:00 | Western | 8 | HVDC | 913
2023-05-30 22:00 | Eastern | 1 | Gas | 5701.79
2023-05-30 22:00 | Eastern | 2 | HFO | 2568
2023-05-30 22:00 | Eastern | 3 | HSD | 393
2023-05-30 22:00 | Eastern | 5 | Hydro | 25
2023-05-30 22:00 | Eastern | 10 | Tripura | 150
2023-05-30 22:00 | Eastern | 12 | Wind | 1
2023-05-30 22:00 | Western | 1 | Gas | 1119
2023-05-30 22:00 | Western | 2 | HFO | 1009
2023-05-30 22:00 | Western | 3 | HSD | 16
2023-05-30 22:00 | Western | 6 | Coal | 2325
2023-05-30 22:00 | Western | 8 | HVDC | 798
2023-05-30 23:00 | Eastern | 1 | Gas | 5628.79
2023-05-30 23:00 | Eastern | 2 | HFO | 2120
2023-05-30 23:00 | Eastern | 3 | HSD | 394
2023-05-30 23:00 | Eastern | 5 | Hydro | 0
2023-05-30 23:00 | Eastern | 10 | Tripura | 150
2023-05-30 23:00 | Eastern | 12 | Wind | 0
2023-05-30 23:00 | Western | 1 | Gas | 1116
2023-05-30 23:00 | Western | 2 | HFO | 961
2023-05-30 23:00 | Western | 3 | HSD | 0
2023-05-30 23:00 | Western | 6 | Coal | 2285
2023-05-30 23:00 | Western | 8 | HVDC | 777